|  |  | TITLE: | ES&H Manual |
| --- | --- | --- | --- |
| DOCUMENT ID: | 3310 Appendix T2 Operational Safety Procedure Form |  |  |

|  | Serial Number: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  | (Assigned by ESH&Q Document Control x7277) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | X | OSP |  |  |  |  |  |  | TOSP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | *Attach the Task Hazard Analysis (THA) related to this procedure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Issue Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Expiration Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (No more than three years from Issue Date except TOSP which is three months from issue date) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Title: |  | HKS Power Supply Commissioning, troubleshooting and operation. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Location: |  |  |  | Hall A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Risk classification (See ESH&Q Manual Chapter 3210 Appendix T3 Risk Code Assignment.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Without mitigation measures (3 or 4): |  |  |  |  |  |  |  |  |  | 4 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | With mitigation measures in place (0, 1, or 2): |  |  |  |  |  |  |  |  |  | 0 |  |  |  |
|  | Document Owner(s): |  |  |  |  |  |  |  | Howard Smith |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  |  |  |  |  |  |  |  |
| Supplemental Technical Validations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hazard Reviewed (per ES&H Manual 2410-T1): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Subject Matter Experts Signature: |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  |  |
|  | Electrical Joe Beaufait |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Fire Chas |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Approval Signatures: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Print Signature |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  |
|  | Division Safety Officer: |  |  |  |  |  |  |  |  | Javier Gomez |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Department or Group Head: |  |  |  |  |  |  |  |  |  |  |  |  | Bob Michaels |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Safety Warden of Area: |  |  |  |  |  |  |  |  |  | Ed Folts |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Other Approval(s): |  |  |  |  |  |  | Joe Beaufait |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Document History: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Revision: |  |  | Reason for revision or update: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Serial number of superseded document |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | New instillation in hall to run experiment. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Distribution: Copies to: affected area, authors, Division Safety Officer, ESH&Q Document Control

After expiration: Forward original and log sheet of trained personnel to ESH&Q Document Control.

|  | - Purpose of the Procedure |  |  |
| --- | --- | --- | --- |
|  | The purpose of procedure is to provide instruction for Technicians to safely commission, troubleshoot and operate HKS power supply. |  |  |
|  | - Scope – include operations, people, and/or areas where procedure applies |  |  |
|  | Installation of HKS power supply to power coils on septum magnet and provide the necessary safeguards to protect personnel and equipment. |  |  |
|  | - Description of the Facility: (include floor plans and layout of a typical experiment or operation) |  |  |
|  | The HKS is a 1254 amp 252 volt water cooled power supply installed into hall to run coils on Septum Magnet. |  |  |
|  | - Authority and Responsibility: |  |  |
|  |  | 4.1 Who has authority to implement/terminate |  |
|  | Electrical and communication connections. Software and communication Howard Smith, Jessie Butler, Heidi Fansler Scott Higgins Jack Segal, Joe Beaufait |  |  |
|  |  | 4.2 Who is responsible for key tasks |  |
|  | Howard Smith Jack Segal |  |  |
|  | - Who analyzes the special or unusual hazards (See ES&H Manual Chapter 3210 Appendix T1 Work Planning, Control, and Authorization Procedure) |  |  |
|  | Ed Folts. Howard Smith. Jack Segal. |  |  |
|  | - Personal and environmental hazard controls including: |  |  |
|  |  | 6.1 Shielding |  |
|  | N/A |  |  |
|  |  | 6.2 Interlocks |  |
|  | Due to the need to drive each coil set on the septum independently, both the HKS and Big Bite power supply faults will be interlocked together back to EESSAF to prevent beam steering problems. - Platform Gate access interlock. - Septum magnet temperatures interlock. - BigBox power supply fault interlock. |  |  |
|  |  | - Other |  |
|  | None |  |  |
|  | - Monitoring systems |  |  |
|  | Once the HKS power supply has been enabled, the power supply can be controlled and monitored locally or remotely with the HKS GUI. |  |  |
|  | - Ventilation |  |  |
|  | Free Air and LCW |  |  |
|  | - List of safety equipment (i.e: personal protective equipment or special tools) |  |  |
|  | - Locks and Tags. - VOM meter. - Non contact Voltage meter. - Safety Glasses. - Necessary arc flash attire. |  |  |
|  | - Associated administrative procedures |  |  |
|  | Make entries into Hall A Log to keep operations and Hall techs informed. |  |  |
|  | - Operating guidelines |  |  |
|  | In accordance to agreed upon Power supply current level set for experiment. |  |  |
|  | - Notification of Affected Personnel (How and Who) |  |  |
|  | Hall A Tech on call procedure |  |  |
|  | - List of steps required to execute the procedure from start to finish. |  |  |
|  | See Attached Procedure. |  |  |
|  | - Back out procedures, i.e., steps necessary to restore the equipment/area to a safe level. |  |  |
|  | Power Down power supply, lock and tag out main power if authorized to do so. |  |  |
|  | - Special environmental control requirements: |  |  |
|  | N/A |  |  |
|  | - Environmental Impacts (See EMP-04 Project/Activity/Experiment Environmental Review |  |  |
|  | N/A |  |  |
|  | - Abatement Steps – Secondary Containment, or Special Packaging requirements |  |  |
|  | N/A |  |  |
|  | - Training requirements |  |  |
|  | To work on Power supply electrical one needs to have the necessary Jefferson Lab Training. - Lock Tag and Try (SAF 104). - Electrical Safety (SAF 603A). - Fire Prevention (SAF 603N). - CPR (SAF 105). |  |  |
|  | - Unusual/Emergency procedures e.g., Injury, Fire, Loss of power |  |  |
|  | N/A |  |  |
|  | - Instrument calibration requirements, e.g., safety system/device recertification, RF probe calibration |  |  |
|  | N/A |  |  |
|  | - Inspection schedules |  |  |
|  | None |  |  |
|  | - References/Associated Documentation |  |  |
|  | HKS Supply Operational Manual ( located in the control cabinet door) |  |  |
|  | - List of Records Generated (Include Location / Review and Approved procedure) |  |  |
|  | None |  |  |

Authorized/Trained Individual

| Print Name/Signature | Date |
| --- | --- |
| Jack Segal |  |
| Howard Smith |  |
| Ed Folts |  |
| Jessie Butler |  |
| Heidi Fansler. |  |
| Joe Beaufait |  |

|  | ISSUING AUTHORITY | APPENDIX AUTHOR | APPROVAL DATE | EFFECTIVE DATE | EXPIRATION DATE | REV. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ESH&Q Division | Harry Fanning | 10/05/09 | 01/01/10 | 10/05012 | 0 |  |  |

This document is controlled as an on line file.  It may be printed but the print copy is not a controlled document.  It is the user’s responsibility to ensure that the document is the same revision as the current on line file.  This copy was printed on 7/30/2026.

| Author: |  | Howard W Smith |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: | 9/26/2011 |  |  |  |  | Task #: If applicable |  |  |  |  | Frequency of use: |  |  | Periodically |
| Complete all information. Use as many sheets as necessary |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Task Location: |  |  |  | Hall A |  |  |  |  | Task Title: |  |  | Installation, troubleshooting and operating HKS power supply. |  |  |
| Division: |  |  | Physics |  |  |  |  |  |  | Department: |  |  | Hall A |  |
| Lead Worker: |  |  |  |  | Howard W Smith |  |  |  |  |  |  |  |  |  |
| Mitigation already in place: Standard Protecting Measures Work Control Documents |  |  |  |  |  |  | All exposed 480 and 120 volt AC shielded in control cabinet. |  |  |  |  |  |  |  |

| Sequence of Task Steps | Task Steps/Potential Hazards | Consequence Level | Probability Level | Risk Code (before mitigation) | Proposed Mitigation (Required for Risk Code >2) | Safety Procedures/ Practices/Controls/Training | Risk Code (after mitigation |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | General work on HKS power supply | M | L | 3 | Follow jlab Electrical policies. | Lock Tag and Try | 0 |
| 2 | Work in low voltage (controls) section of the HKS power supply | L | L | 2 | Follow equipment operation manual. | Proper PPE in accordance with this procedure. Equipment specific training | 0 |

|  | Highest Risk Code before Mitigation: | 3 |  | Highest Risk Code after Mitigation: 0 |  |
| --- | --- | --- | --- | --- | --- |

When completed, if the analysis indicates that the Risk Code before mitigation for any steps is “medium” or higher (RC≥3), then a formal Work Control Document (WCD) is developed for the task.  Attach this completed Task Hazard Analysis Worksheet.  Have the package reviewed and approved prior to beginning work.  (See ES&H Manual Chapter 3310 Operational Safety Procedure Program.)

|  | ISSUING AUTHORITY | FORM TECHNICAL POINT-OF-CONTACT | APPROVAL DATE | EFFECTIVE DATE | EXPIRATION DATE | REV. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ESH&Q Division | Harry Fanning | 10/05/09 | 01/01/09 | 10/05/12 | 0 |  |  |

This document is controlled as an on line file.  It may be printed but the print copy is not a controlled document.  It is the user’s responsibility to ensure that the document is the same revision as the current on line file.  This copy was printed on 7/30/2026

- Define the scope of work

- Job Summery

Install HKS power supply to run coils on Septum Magnet

- Affected systems

Electrical power

LCW

Septum Magnet

Beam

2. Analyze Hazard

See attached THA

3. Develop and implement Hazard controls

- List of PPE

Safety Glasses

Locks and Tags

Appropriate Arc Flash PPE

- Identify danger zones

Electrical shock and or equipment damage due to supplied 480 volt main power.

Electrical shock and or equipment damage due to stored internal capacitor energy.

Arc Flash Hazard.

Fire

- Training required

Lock Tag and Try (SAF 104).

Electrical Safety (SAF 603A).

Fire Prevention (SAF 603N).

CPR (SAF 105).

4. Perform work within controls

- Number of people needed

Two Electrically certified workers should be present when locking and tagging out equipment.

- Verify  that needed training is completed and current

Persons working on or about HKS power supply must have appropriate Jefferson lab training to be an Electrical worker.

- List of materials

Locks and Tags.

VOM meter.

Noncontact voltage detector.

Phase Rotation Meter

Schematics/Operation Manual.

Tools (wrenches, screwdrivers, flashlight etc.).

- Procedure

Commissioning HKS

    - Perform pre-job briefing (1st step).

    - Ensure that all electrical connections are torque properly.

    - Make sure that there is adequate LCW pressure (142 lb.) and flow.

    - Verify voltage and phase rotation of main power.

    - Check for and clear all internal power supply faults.

    - Confirm that the power supply can be controlled locally.

    - Authenticate remote communications to power supply.

    - Insure that all external faults (interlocks) are functioning properly.

    - Validate voltage and current stability.

Any major work done to the HKS power supply must be authorized by Joe Beaufait.

- Post job briefing and cleanup

Operating HKS.

- Before operating power supply one must read and understand this document and complete training on power supply operation by Hall A technical staff.

- Read and sign conduct of operation for G2P experiment.

- Check with Hall A work coordinator to verify that the HKS power supply is operational.

- Ensure that it is safe to operate power supply by communicating with all affected personnel working in the general area around Septum magnet and Target.

- Verify that all access gates leading to Septum magnet/Target platform are closed.

- Using the GUI for HKS power supply turn on power supply and reset to clear faults; if faults do not clear a manual reset will have to be initiated by depressing Estop.

- If faults still do not clear, inform Hall A Techs (Tech on call procedure).

- Set desired current needed for operation. (There are two modes of controlling HKS power supply output current in software; through individual current settings or by setting momentum. Additionally, do not adjust current while taking beam, only a Primary Spokesperson can authorize current changes while taking Beam. ).

- Power supply must be operated within the agreed upon parameters set by Primary Spokespersons.

- For any issues concerning Septum magnet refer to Septum magnet OSP.

5. Provide feedback and continuous improvement.

Document any mistakes, corrections, changes and pictures and implement changes. Turn in feedback to Hall work coordinator