## JLAB
Magnet Name | Nom. Op Current (A) | Max Op Current (A) | Peak Current (A) | Nominal Voltage (V) | L (mH) | R (ohms)
US Torus | 1075 | 1182.5 | 1290 | 77.5 | 0.631 | 0.059
DS Torus - 1 | 2230 | 2453 | 2676 | 40 | 0.153 | 0.015
DS Torus - 2 | 2440 | 2684 | 2928 | 42 | 0.246 | 0.013
DS Torus - 3 | 3235 | 3558.5 | 3882 | 57 | 0.348 | 0.013
DS Torus - 4 | 3350 | 3685 | 4020 | 224 | 3.051 | 0.056
AC Input
Disconnect Switch Enclosure | Should be NEMA 250 Type 12 | Hazard Label | Should be in separate enclosure | No exposed terminals
Disconnect Switch | UL98 | Padlock | VVU to monitor load side of the switch | Max cable size 750MCM w max 500A per cable
Main Contactor | Actuator activated Ckt breaker not acceptable | Atleast 4 Aux to monitor the status of main contacts | Aux contacts meet IEC 60-947 | 2 NO & 2 NC | AC OV and OC must be included

## OCEM
Compiled by | P K Ghoshal
Tech team - | P Ghoshal (TR), D Kashy (TL), O. Kumar (DC Power), N Sandoval (Fast electronics), J Segel (Detector sys Lead), R Adrover (Electrical Safety)
Support - | J Fast (PM-Moller), M Bevins (CAM Spectrometer), R Wines (PE-Moller), S Philip (Head DC Power), T Fitzgerald (Head - Electrical safety)
Reference Doc- | PMAG0000-0100-S0014 MOLLER MPS specification (Approved document)
Location of document @ JLAB (Internal reference only): O:\Magnet_Design_Tools\Magnet Projects\MOLLER - Hall A\6. Engineering Calculations-Analyses-Simulations\Electrical\Magnet Power supply_Normal\Moller MPS OCEM
Date - | 2022-02-25
OCEM has a sister company named Multi Electric located in Chicago! | [11 empty] | Leadtimes
[9 empty] | Leadtimes |  |  | Hi-potting of Chokes? | Improve reliability due to use of Film capacitors!
| Topology | Max P rating per module (W) | Max I Ratings per Module | Max V rating per module | Switching Freq (Hz) | # of Parallel IGBT modules | IGBT rated Voltage (V) | IGBT size (mm/inches) | IGBT part# or Family | IGBT Power dissipation? | IGBT current sharing? | Choke Value; also what kind of cooling | DC Filter Capacitor Type | IGBT Driver | Diagnostic signal names and functions? Can we ask for more diagnostic signals if needed? | Cooling plate used (what flow?)
Per module Spec | Buck | 83K | 1200 | 93 | 10K | 3 | 650 | 150x62x17/5.9x2.44x0.67 | The IGBT drivers are off-the-shelf from Power Integration – model 2SP0115T2Ax-06, data sheet provided (“2SP0115T2Ax-06.pdf”). |  |  |  | Ducati/AVX/Kemet/Electronicon film capacitors designed for DC-bus applications (low ESL and ESR). Specific and/or alternative manufacturer can be discussed during the detailed design phase. As example AVX series FFVS. Datasheet provided “FFVS.pdf”. | 2SP0115T |  | Copper & Stainless steel in contact with water
OCEM Tech offer
Magnet Name | # of converters | Peak Current | Max Voltage (V) | Rated Power (kW)
US Torus |  | 1290 | 93 | 84
DS Torus - 1 |  | 2676 | 48 | 90
DS Torus - 2 |  | 2928 | 50.4 | 103
DS Torus - 3 |  | 3882 | 68.4 | 185 | 1st to be recd in Q3 FY2022 (Nov/Dec 2022)
DS Torus - 4 |  | 4020 | 269 | 751
Main PS | FPGA with SOC | DSP | Control Electronics | Communication |  |  | DCCT | Ramp Rates? | Mechanical | Internal Flow meters? | Free wheeling diodes? | Shielding? | Before critical component buy | Stored energy cal
Control board | Xilinx's Zynq (used for Digital Output control algorithms) | T.I. (for high resolution PWM generation) | Co developed with CAENels | Ethernet either TCP-IP or UDP | Embedded Linux OS with EPICS driver on board the PS | VISUAL PS software | 0-Flux (Danisense/LEM) | Configurable? | How cables are routed? Burbar or breaded cables (Shielding) | If yes, are they interlocked? | How is this done? Are you using diode from the buck converter | How PWM signal goes to individual module from control board | Should we get dataheets of critical component order?
Main PS | ADC | Other ADC | I/O |  |  | PS for Active DCCT
Carrier board | 2x24-bit @ 100Ksps for I & V (also temperature stabalized) | 16-bit @ 100Ksps for (DC-link, temperature & Aux analog readings) | I/O signals | Interlocks and status signals | Future expansion connnector | Low noise +/-15V
Interlock scheme/schematics :
1. The NGPS manuals show (4) software configurable interlocks, but we also have hardwire interlocks in proposal.
2. How does the software configurable vs hardwire interlock functionally differ ? (Especially as it scales across multiple modules)
3. Preference for water flow meters over switches to monitor build up across different circuits
Controller/Interface :
1. How is priority given to remote interfaces(web ASCII, IOC, SFP)?
2. Can we configure safe shutdown in case of loss of communication from preferred interface?
3. How will the 100ksps 24bitadc and 16bitadc signals be made available?
4. Do we have ability to configure all necessary parameters in case of controller failure, IE one spare controller can operate any of the 5 power supplies.
LCW Line
1. Pressure testing
2. Required to meet the ASME/B13.3 and 13.9 as applicable. Any qyualifications or requirments.
3. Attachement II - Water Cooling Hardware & Considerations
4. LCW Line Inlet to be from underneath the MPS with AC and DC (input/Output) from the top)
Enclosure compliance
1. IP20 compliance to be discussed as mentioned, how you intend to comply with NEMA12?
Ans 1. We can offer an IPx2 cabinet that is protected against direct sprays of water up to 15° from the vertical. This is equivalent to NEMA12. (To be discussed for cmpliancy)
2. Are the transformers for the input UL or CE rated?
Ans 2. The transformers will be designed according to the IEC standards by a company that is compliant with the UL transformers manufacturing methods and materials. The UL materials list of the insulation system of the transformer will be provided.
3. Excplicity the final foot print and height for all MPS