## HB-Chassis Layout
PLC I/O Usage Table
Magnets | [8 empty] | 8 Channels
Module | IV16 | OF4 | OW16I | OW16I | IF16 | IF16 | IF16 | IF16 | IF16
Configuration |  | 0-5 volts output |  |  | Single_Ended voltage | Single_Ended Voltage/Current | Single_Ended_Mode Voltage | Differential_Mode Current | Differential_Mode Voltage
Chasis Slot # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Channel
0 | QD_U1 | Setpnt_m_flow_LCL | MOT_JTV1_Close | He_CG_Current_enabled | TP_He_PT_1 | TR_Coil_1 | SG_1 | LVDT_JTV1 | Current Lead R
1 | QD_L1 | Setpnt_m_flow_RCL | MOT_JTV1_Open | Vacuum_power | TP_He_PT_2 | TR_Coil_2 | SG_2 | LVDT_JTV2 | Coil 1
2 | QD_U2 |  | MOT_JTV2_Close | Keep_Alive_Reset | TP_He_PT_3 | TR_Coil_3 | SG_3 | LVDT_JTV3 | Coil 2
3 | QD_L2 |  | MOT_JTV2_Open | Keep_Alive_Control | TP_He_PT_4 | TR_Coil_4 | SG_4 | LVDT_JTV4 | Current Lead L
4 | QD_U3 |  | MOT_JTV3_Close | Power_liquid_level_meter | TP_LN2_OT | TR_He_LCLC | SG_5 | LVDT_JTV5
5 | QD_L3 |  | MOT_JTV3_Open | PLC_Fast_Relay | TP_LN2_OB | TR_He_RCLC | SG_6 | LVDT_JTV6
6 | QD_U4 |  | MOT_JTV4_Close | PLC_Slow_Relay | TP_LN2_BT | TR_LHe_Resv | SG_7 | Warm_Return_Position
7 | QD_L4 |  | MOT_JTV4_Open | MPS_CPU_Reset | TP_LN2_BB | TR_Aux-Vessel | SG_8 | LL He & LN2
8 | QD_Sum |  | MOT_JTV5_Close | MPS_diodes_Reset | TP_LN2_IN | Vac | SG_9 | N/A | N/A
9 | He_LL_alarm |  | MOT_JTV5_Open | Danf_QD_Reset | TP_LN2_Ret | p_He | SG_10 | N/A | N/A
10 | LN2_LL_alarm |  | MOT_JTV6-Close | He /LN2 LL select | TP_He_LCLW | p_N2 | SG-11 | N/A | N/A
11 | JVT Mtrs KS remote |  | MOT_JTV6_Open | Diode_Current_enabled | TP_He_RCLW | m_flow_LCL | SG-12 | N/A | N/A
12 | PSU_Control_pwr_on |  | Warm_return_Close |  | TD_LHe_CD | m_flow_RCL |  | N/A | N/A
13 | PSU_Main_pwr_on |  | Warm_return_Open |  | TD_LHe_Supply | MPS_Current_Signal |  | N/A | N/A
14 | PSU_ready |  |  |  | TD_LHe_Ret | Hall Probe |  | N/A | N/A
15 | PSU_Sum_Interlocks |  |  |  | TD_LHe_WR | LL-He 2 |  | N/A | N/A
Dataforth Signal Conditioner Table SCM5B modules
Rack
Channel |  |  |  |  | 3 | 1 | 5 |  | 6
1 |  |  | JT1 LN2 Cooldown |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
2 |  |  | JT2 LN2 Top Fill |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
3 |  |  | JT3 He Cooldown |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
4 |  |  | JT4 He Bottom Fill |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
5 |  |  | JT5 He Top Fill |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V]
6 |  |  | JT6 He Cold Return |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V]
7 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V]
8 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V]
Channel |  |  |  |  | 2 | 4 | 6
1 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 31-03D [+/-10V - +/-10V]
2 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 38-35D [+/-20mV - +/-10V]
3 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 38-35D [+/-20mV - +/-10V]
4 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 31-03D [+/-10V - +/-10V]
5 |  |  |  |  | 43-05D [+/-5V - +/-10V] | 31-03D [+/-10V - +/-10V] | 38-35D [+/-20mV - +/-10V]
6 |  |  |  |  | 43-05D [+/-5V - +/-10V] | 31-03D [+/-10V - +/-10V] | 38-35D [+/-20mV - +/-10V]
7 |  |  |  |  | 43-05D [+/-5V - +/-10V] | ?? | 38-35D [+/-20mV - +/-10V]
8 |  |  |  |  | 43-05D [+/-5V - +/-10V] | ?? | 38-35D [+/-20mV - +/-10V]

## SHMS Control Summary
SHMS PLC Controls for magnets, carriage rotation, Cryo systems and vacuum
| 2007 Budget | PR estimates | Components as of 11/2013 | Change
from sub-sheets
PLC Modules & Software | 107593.78 |  | 112662.34 | 4.711%
Signal Conditioners | 92251 |  | 86240.5 | -6.515%
Racks/Termination and Cables | 238168.6 |  | 90823.72 | -61.87% | Initial Wiring ran from Hall to 2nd floor counting house over 500ft, Cost of copper in 2007 was higher than when purchased in 2012, Used surplus racks and other hardware
Instrumentation Hardware | 110282 |  | 115303.74 | 4.554%
Total Five magnet + Heat exchanger | 548295.38 | 603313.57 | 405030.3 | -26.13%
|  | PO's awarded | 403865.06
|  | PO's queued | 4800 | Value of components not listed in sub-sheets
|  | Total PO charges | 408665.06 | 3634.76

## PLC Modules Software
|  | Date 2/07/2007 |  | 0.74
JEFFERSON LAB CONTROLOGIX REDUNDANCY PROJECT PROPOSAL
Qty | Catalog # | Description | Price | Ext. Price
Fiscal Year 20120
|  | Software |  |  | Summary of Software: |  |  |  | Date | PO | Ordered | unit Cost | Total Cost
0 | 9324RLD700NXENE | RS-Logix 5000 Pro Edition | 5500 | 0 | 9324RLD700NXENE | RS-Logix 5000 Pro Edition
0 | 9701-VWSTENE | RSVIEW Studio | 2000 | 0 | 9701-VWSTENE | RSVIEW Studio
1 | 9701-VWSS000LENE | RSView Enterprise unlimited displays *(Trade in not shown) | 15000 | 15000 | 9701-VWSS100LENE | RSView Enterprise unlimited displays |  |  | 2013-02-13 | 13-P1308 | 1 | 8440 | 8440
1 | 9701-VWSCWAENE | SE Client | 2200 | 2200 | 9701-VWSCWAENE | SE Client
0 | 9301-OPCSRVENE | KPServer | 2000 | 0
0 | 9356PRO2100 | RSSQL Prof 150 Tags | 2800 | 0 | [7 empty] | sub-Total | 8440
|  |  | Subtotal: | 17200
[5 empty] | Summary of Hardware: |  |  |  | Date | PO | Ordered | Unit Cost | Total Cost
|  | Subsystem of New System : Redundant CLX |  |  | 1756-L62M | LOGIX5562 PROCESSOR WITH 4 MBYTE NV MEMORY |  |  | 2010-03-10 | 10-P1267 | 2 | 5626.96 | 11253.92
2 | 1756-A7 | 4 SLOT CONTROLLOGIX CHASSIS | 442 | 884 | 1757-SRC1 | 1757 REDUNDANCY MODULE CABLE - 1 METER, 3.28FT |  |  | 2010-03-10 | 10-P1267 | 1 | 111 | 111
4 | 1756-CNB | CONTROLNET BRIDGE MODULE | 1312 | 5248 | 1757-SRM | SYSTEM REDUNDANCY MODULE |  |  | 2010-03-10 | 10-P1267 | 2 | 3422.5 | 6845
2 | 1756-ENBT | CLX ETHERNET/IP 10/100 BRIDGE MODULE - TWISTED PR | 1760 | 3520 | 1756-CNB | CONTROLNET BRIDGE MODULE |  |  | 2010-03-10 | 10-P1267 | 8 | 1457.8 | 11662.4
2 | 1756-L62M | LOGIX5562 PROCESSOR WITH 4 MBYTE NV MEMORY | 8457 | 16914 | 1756-ENBT | CLX ETHERNET/IP 10/100 BRIDGE MODULE - TWISTED PR |  |  | 2010-03-10 | 10-P1267 | 2 | 1962.48 | 3924.96
2 | 1756-N2 | EMPTY SLOT FILLER CARD (ONE FILLER PER PACKAGE) | 21 | 42 | 1756-N2 | EMPTY SLOT FILLER CARD (ONE FILLER PER PACKAGE) |  |  | 2010-03-10 | 10-P1267 | 2 | 19.24 | 38.48
2 | 1756-PA72 | 85-265 VAC POWER SUPPLY (5V @ 10 AMP) | 805 | 1610 | 1756-PA72 | 85-265 VAC POWER SUPPLY (5V @ 10 AMP) |  |  | 2010-03-10 | 10-P1267 | 8 | 623.08 | 4984.64
1 | 1757-SRC1 | 1757 REDUNDANCY MODULE CABLE - 1 METER, 3.28FT | 156 | 156 | 1786-XT | CONTROLNET 75 OHM TERMINATOR PLUG |  |  | 2010-03-10 | 10-P1267 | 2 | 6.66 | 13.32
2 | 1757-SRM | SYSTEM REDUNDANCY MODULE | 4860 | 9720 | 1786-TPS | CONTROLNET T-TAP/STRAIGHT |  |  | 2010-03-10 | 10-P1267 | 14 | 81.4 | 1139.6
2 | 1786-XT | CONTROLNET 75 OHM TERMINATOR PLUG | 7 | 14 | 1756-TBCH | 36 PIN SCREW CLAMP BLOCK WITH STANDARD HOUSING |  |  | 2010-03-10 | 10-P1267 | 54 | 56.98 | 3076.92
14 | 1786-TPS | CONTROLNET T-TAP/STRAIGHT | 99 | 1386 | 1756-TBNH | 20 NEMA Screw Clamp Block |  |  | 2010-03-10 | 10-P1267 | 4 | 45.88 | 183.52
1 | 1786-RG6 | CONTROLNET RG6 SHIELD HIGH FLEX CABLE-1000FT ROLL | 568 | 568 | 1756-IV16 | DC (10-30V) Sourcing Input Module |  |  | 2010-03-10 | 10-P1267 | 5 | 244.94 | 1224.7
|  |  | Subtotal: | 40062 | 1756-DNB | Device net Bridge |  |  | 2010-03-10 | 10-P1267 | 1 | 806.6 | 806.6
[5 empty] | 1756-OW16I | N.O. ISOLATED RELAY OUTPUT 16 PTS (36 PIN) |  |  | 2010-03-10 | 10-P1267 | 12 | 427.72 | 5132.64
|  | Subsystem of New System : Bender Dipole I/O |  |  | 1756-IF16 | ANALOG INPUT - CURRENT/VOLTAGE 16 PTS (36 PIN) |  |  | 2010-03-10 | 10-P1267 | 30 | 1065.6 | 31968
1 | 1756-A10 | 10 SLOT CONTROLLOGIX CHASSIS | 542 | 542 | 1756-A7 | 7 slot chassis |  |  | 2010-03-10 | 10-P0996 | 2 | 344.1 | 688.2
1 | 1756-CNB | CONTROLNET BRIDGE MODULE | 1312 | 1312 | 1756-A10 | 10 slot chassis |  |  | 2010-03-10 | 10-P0996 | 6 | 420.32 | 2521.92
1 | 1756-IV16 | 79-132 VAC INPUT 16 PTS (20 PIN) | 408 | 408 | 1756-OG16 | 0-5 TTL output |  |  | 2010-03-10 | 10-P0996 | 2 | 316.72 | 633.44
1 | 1756-IB16D | 16 channel Digital Input Module | 1397 | 1397 | MVI94-GSC | Prosoft ASCII Generic Serial Communication Module |  |  | 2012-01-17 | 12-P0810-0 | 5 | 1060 | 5300
2 | 1756-OW16I | N.O. ISOLATED RELAY OUTPUT 16 PTS (36 PIN) | 559 | 1118 | 1794-ACN15 | SINGLE MEDIA ADAPTER FOR CONTROLNET |  |  | 2012-01-17 | 12-P0810-0 | 1 | 472.68 | 472.68
5 | 1756-IF16 | ANALOG INPUT - CURRENT/VOLTAGE 16 PTS (36 PIN) | 1397 | 6985 | 1794-PS13 | 85-264 VAC TO 24 VDC 1.3A POWER SUPPLY |  |  | 2012-01-17 | 12-P0810-0 | 1 | 135 | 135
1 | 1756-PA72 | 85-265 VAC POWER SUPPLY (5V @ 10 AMP) | 805 | 805 | 1756-IF4FXOF2F | 4 channel Hi speed buffered Input |  |  | 2013-10-31 | 337708 | 2 | 2400 | 4800
9 | 1756-TBCH | 36 PIN SCREW CLAMP BLOCK WITH STANDARD HOUSING | 67 | 603 | 800T-J91A | 3 position switch |  |  | 2012-01-17 | 12-P0810-0 | 2 | 72 | 144
1 | 1794-ACN15 | SINGLE MEDIA ADAPTER FOR CONTROLNET | 671 | 671 | 800T-H33B | 2 position |  |  | 2012-01-17 | 12-P0810-0 | 1 | 132 | 132
1 | 1794-PS13 | 85-264 VAC TO 24 VDC 1.3A POWER SUPPLY | 190 | 190 | 1489-A2C020 | Circuit Breaker 2A |  |  | 2012-01-17 | 12-P0810-0 | 2 | 56 | 112
1 | MVI94-GSC | Prosoft ASCII Generic Serial Communication Module | 1056 | 1056 | 1489-A2C050 | Circuit Breaker 5A |  |  | 2012-01-17 | 12-P0810-0 | 1 | 56 | 56
|  |  | Subtotal: | 15087 | 1489-A2C100 | Circuit Breaker 10A |  |  | 2012-01-17 | 12-P0810-0 | 1 | 56 | 56
[5 empty] | 1492-JD3 | AB end anchor |  |  | 2012-01-17 | 12-P0810-0 | 30 | 1.58 | 47.4
|  | Subsystem of New System : Quadrupole 1 |  |  | 1492-EAJ35 | AB double terminal block |  |  | 2012-01-17 | 12-P0810-0 | 50 | 2.58 | 129
1 | 1756-A10 | 10 SLOT CONTROLLOGIX CHASSIS | 542 | 542 | 1783-US08T | Ethernet switch |  |  | 2013-01-08 | 13-M0462-0 | 1 | 260 | 260
1 | 1756-CNB | CONTROLNET BRIDGE MODULE | 1312 | 1312 | 1756-EN2T | Control Logix Ethernet/IP module |  |  | 2013-01-08 | 13-M0462-0 | 1 | 2124 | 2124
1 | 1756-IV16 | 79-132 VAC INPUT 16 PTS (20 PIN) | 408 | 408 | 1756-OF4 | 4 output voltage or current |  |  | 2010-04-24 | 10-P2174-0 | 5 | 849 | 4245
1 | 1756-IB16D | 16 channel Digital Input Module | 1397 | 1397
2 | 1756-OW16I | N.O. ISOLATED RELAY OUTPUT 16 PTS (36 PIN) | 559 | 1118
5 | 1756-IF16 | ANALOG INPUT - CURRENT/VOLTAGE 16 PTS (36 PIN) | 1397 | 6985
1 | 1756-PA72 | 85-265 VAC POWER SUPPLY (5V @ 10 AMP) | 805 | 805
9 | 1756-TBCH | 36 PIN SCREW CLAMP BLOCK WITH STANDARD HOUSING | 67 | 603
1 | 1794-ACN15 | SINGLE MEDIA ADAPTER FOR CONTROLNET | 671 | 671
1 | 1794-PS13 | 85-264 VAC TO 24 VDC 1.3A POWER SUPPLY | 190 | 190 | [7 empty] | Total | 112662.34
1 | MVI94-GSC | ProSoft ASCII Generic Serial Communication Module | 1056 | 1056
|  |  | Subtotal: | 15087 |  | Total Software & Hardware
[6 empty] | Budgeted | 107593.78
|  | Subsystem of New System : Quadrupole 2 |  |  | 2013-11-07 | Spent | 112662.34 | 4.711%
1 | 1756-A10 | 10 SLOT CONTROLLOGIX CHASSIS | 542 | 542
1 | 1756-CNB | CONTROLNET BRIDGE MODULE | 1312 | 1312
1 | 1756-IV16 | 79-132 VAC INPUT 16 PTS (20 PIN) | 408 | 408
1 | 1756-IB16D | 16 channel Digital Input Module | 1397 | 1397
2 | 1756-OW16I | N.O. ISOLATED RELAY OUTPUT 16 PTS (36 PIN) | 559 | 1118
5 | 1756-IF16 | ANALOG INPUT - CURRENT/VOLTAGE 16 PTS (36 PIN) | 1397 | 6985
1 | 1756-PA72 | 85-265 VAC POWER SUPPLY (5V @ 10 AMP) | 805 | 805
9 | 1756-TBCH | 36 PIN SCREW CLAMP BLOCK WITH STANDARD HOUSING | 67 | 603
1 | 1794-ACN15 | SINGLE MEDIA ADAPTER FOR CONTROLNET | 671 | 671
1 | 1794-PS13 | 85-264 VAC TO 24 VDC 1.3A POWER SUPPLY | 190 | 190
1 | MVI94-GSC | ProSoft ASCII Generic Serial Communication Module | 1056 | 1056
|  |  | Subtotal: | 15087
Subsystem of New System : Quadrupole 3
1 | 1756-A10 | 10 SLOT CONTROLLOGIX CHASSIS | 542 | 542
1 | 1756-CNB | CONTROLNET BRIDGE MODULE | 1312 | 1312
1 | 1756-IV16 | 79-132 VAC INPUT 16 PTS (20 PIN) | 408 | 408
1 | 1756-IB16D | 16 channel Digital Input Module | 1397 | 1397
2 | 1756-OW16I | N.O. ISOLATED RELAY OUTPUT 16 PTS (36 PIN) | 559 | 1118
5 | 1756-IF16 | ANALOG INPUT - CURRENT/VOLTAGE 16 PTS (36 PIN) | 1397 | 6985
1 | 1756-PA72 | 85-265 VAC POWER SUPPLY (5V @ 10 AMP) | 805 | 805
9 | 1756-TBCH | 36 PIN SCREW CLAMP BLOCK WITH STANDARD HOUSING | 67 | 603
1 | 1794-ACN15 | SINGLE MEDIA ADAPTER FOR CONTROLNET | 671 | 671
1 | 1794-PS13 | 85-264 VAC TO 24 VDC 1.3A POWER SUPPLY | 190 | 190
1 | MVI94-GSC | ProSoft ASCII Generic Serial Communication Module | 1056 | 1056
|  |  | Subtotal: | 15087
Subsystem of New System : Dipole I/O
1 | 1756-A10 | 10 SLOT CONTROLLOGIX CHASSIS | 542 | 542
1 | 1756-CNB | CONTROLNET BRIDGE MODULE | 1312 | 1312
1 | 1756-IV16 | 79-132 VAC INPUT 16 PTS (20 PIN) | 408 | 408
1 | 1756-IB16D | 16 channel Digital Input Module | 1397 | 1397
2 | 1756-OW16I | N.O. ISOLATED RELAY OUTPUT 16 PTS (36 PIN) | 559 | 1118
5 | 1756-IF16 | ANALOG INPUT - CURRENT/VOLTAGE 16 PTS (36 PIN) | 1397 | 6985
9 | 1756-TBCH | 36 PIN SCREW CLAMP BLOCK WITH STANDARD HOUSING | 67 | 603
1 | MVI94-GSC | Prosoft ASCII Generic Serial Communication Module | 1056 | 1056
|  |  | Subtotal: | 13421
Subsystem of New System : Cryogenics/Other
1 | 1756-A10 | 10 SLOT CONTROLLOGIX CHASSIS | 542 | 542
1 | 1756-CNB | CONTROLNET BRIDGE MODULE | 1312 | 1312
2 | 1756-IB16D | 16 channel Digital Input Module | 542 | 1084
5 | 1756-IF16 | ANALOG INPUT - CURRENT/VOLTAGE 16 PTS (36 PIN) | 1397 | 6985
2 | 1756-OW16I | N.O. ISOLATED RELAY OUTPUT 16 PTS (36 PIN) | 559 | 1118
1 | 1756-PA72 | 85-265 VAC POWER SUPPLY (5V @ 10 AMP) | 805 | 805
9 | 1756-TBCH | 36 PIN SCREW CLAMP BLOCK WITH STANDARD HOUSING | 67 | 603
1 | 1794-ACN15 | SINGLE MEDIA ADAPTER FOR CONTROLNET | 671 | 671
1 | 1794-PS13 | 85-264 VAC TO 24 VDC 1.3A POWER SUPPLY | 190 | 190
1 | MVI94-GSC | Prosoft ASCII Generic Serial Communication Module | 1056 | 1056
|  |  | Subtotal: | 14366
|  |  | Total | 145397
|  |  | Discounted Total | 107593.78
Note on D24: Steven Lassiter:
Note on D25: Steven Lassiter:

## Signal Conditioners
|  |  |  | DataForth Signal Conditioners | Date Oct. 20, 2006
| Qty | Qty | Catalog # | Description | Price | Price/magnet | total price
| per | per |  |  |  | 1 | plus spares
Spares | HB | magnet |  | Magnets |  |  |  | Date | PR/PO | Ordered | unit Cost | Total Cost | Used | Returned
4 | 12 | 12 | SCM5B-34-1562 | RTD custom | 265 | 3180 | 16960 | 3/3/210 | 289237 / 10-P1266 | 64 | 265 | 16960 | 60
7 | 7 | 7 | SCM5B-30-02D | Analog Input Narrow bandwidth 50mV in / 10V out | 140 | 980 | 5880 | 3/3/210 | 289237 / 10-P1266 | 42 | 140 | 5880 | 35
0 | 0 | 3 | SCM5B-31-03D | Analog Voltage Input Module 10V in / 10V out | 150 | 450 | 1650 | 3/3/210 | 289237 / 10-P1266 | 11 | 150 | 1650 | 11 |  | 53328.5
2 | 4 | 1 | SCM5B-31-03D | Analog Voltage Input Module 10V in / 10V out | 160 | 160 | 1600 | 3/3/210 | 299653 / 11-M0748 | 11 | 150 | 1650 | 9
|  | 8 | SCM5B-31-09D | Analog Voltage Input Module 40V in / 10V out | 160 | 1280 | 5120 | 3/3/210 | 289237 / 10-P1266 | 42 | 140 | 5880 | 40
0 | 12 | 10 | SCM5B-38-35D | Strain Gage Input Module | 162 | 1620 | 8424 | 3/3/210 | 289237 / 10-P1266 | 52 | 162 | 8424 | 52
2 | 4 | 4 | SCM5B-43-05D | General Purpose with excitation 5V in / 10V out | 205 | 820 | 4510 | 3/3/210 | 289237 / 10-P1266 | 22 | 205 | 4510 | 20
0 | 6 | 6 | SCMXCA-004 12 | Cable | 35 | 210 | 1050 | 3/3/210 | 289237 / 10-P1266 | 30 | 35 | 1050 | 30
0 | 6 | 6 | SCMPB-05-02 | Backplane-8 channels with DIN mounts | 227 | 1362 | 6810 | 3/3/210 | 289237 / 10-P1266 | 30 | 227 | 6810 | 30
0 | 6 | 6 | SCMXIF-DIN | Breakout Board Din Mounted | 63 | 378 | 1890 | 3/3/210 | 289237 / 10-P1266 | 30 | 63 | 1890 | 30
30 | 6 | 6 | SCMXRK-002 | Rack Mounting Plate 19" | 61 | 366 | 3660 | 3/3/210 | 289237 / 10-P1266 | 30 | 61 | 274.5 | 0 | 30
34 | 6 | 6 | LVC-2500 | LVDT signal conditioner 24Vdc | 425 | 2550 | 27200 | 3/3/210 | 289228 / 10-P1264 | 64 | 425 | 27200 | 30
1 | 1 | 1 | SDP5-5-100T | PSU 5 volts | 92.4 | 92.4 | 554.4 | 3/3/210 | 289255 / 10-P1249 | 6 | 92.4 | 554.4 | 5
2 | 2 | 2 | SDN10-24-100P | PSU 24V Psu | 292.3 | 584.6 | 3507.6 | 3/3/210 | 289255 / 10-P1249 | 12 | 292.3 | 3507.6 | 10
Heat Exchanger
|  | 1 | SCMPB-05-02 | Backplane-8 channels with DIN mounts | 227 |  | 227 | 2012-01-17 | 314009/12-M0772-0 | 1 | 252 | 252 | 1
|  | 1 | SCMXCA-004 12 | Cable | 35 |  | 35 | 2012-01-17 | 314009/12-M0772-0 | 1 | 35 | 35 | 1
|  | 1 | SCMXIF-DIN | Breakout Board Din Mounted | 63 |  | 63 | 2012-01-17 | 314009/12-M0772-0 | 1 | 63 | 63 | 1
|  | 8 | SCM5B-43-05D | General Purpose with excitation 5V in / 10V out | 205 |  | 1640 | 2012-01-17 | 314009/12-M0772-0 | 8 | 211 | 1688 | 8
|  | 2 | LVC-2500 | LVDT signal conditioner 24Vdc | 425 |  | 850 | 2012-01-17 | 314012/12-M0773-0 | 2 | 425 | 850 | 2
|  | 4 | SCM5B-30-07D | Analog Voltage Input Module 1V in / 10V out | 155 |  | 620 | 2013-01-25 | 326834/ CC | 4 | 155 | 620 | 4
[7 empty] | Budget |  |  |  |  | Spent
[5 empty] | Subtotal: |  | 92251 |  |  |  |  | 86240.5 | -6.515%
restocking fee

## Rack Termination cabling
Date 2/07/2007
|  | I/O Rack / Hardware / Cable per Magnet |  |  |  |  | Date | PR/PO | Ordered | unit Cost | Total Cost
Qty per magnet/rack | Catalog # | Description | Price | Disc. Price | Ext. Price
1
|  | Rack Chassis |  | 0.737
1 | XFR-317824 | Vertical Frame 31.562 deep 82.375 Tall 27.562 wide | 663.52 | 663.52 | 663.52
4 | XMA-78 | Mounting Angle Pair | 45 | 45 | 180
1 | XPN-7324 | Panel 73.5" Tall 24" wide | 105 | 105 | 105
1 | DS-XSR-7824 | Front Door | 160 | 160 | 160
1 | DS-XSL-7824 | Rear Door | 160 | 160 | 160
1 | XES-2024 | Equipment Shelf | 36 | 36 | 36
2 | XSP-3178-S | Side Panel | 130 | 130 | 260
1 | XPN-2819 | Top Panel | 40 | 40 | 40
2 | XPN-0324-CAP | Data Cable Access Panel | 28 | 28 | 56
100 | HW-092 | Threaded captive clip nut | 0.4 | 0.4 | 40
100 | HW-103 | #10-32 thread truss head machine screw | 0.28 | 0.28 | 28
1 | 446149 | Latch/Slotted | 4 | 4 | 4
1 | A423008LP | SINGLE DOOR ENCLOSURE HOFFMAN | 750 | 750 | 750
1 | a42p30 | PANEL FOR ENCLOSURE | 175 | 175 | 175
3 | ABA-05 | Panel reducers | 51 | 51 | 153
|  |  | Subtotal: |  | 2810.52 | 14052.6
|  | Rack hardware |  |  |  |  | Date | PR/PO | Ordered | unit Cost | Total Cost
800 | 1492-W4 | Terminal Blocks Single Level | 1.55 | 1.55 | 1240 |  | 2010-03-03 | 289237 / 10-P1267 | 2000 | 0.71 | 1420
100 | 1492-WD3 | Terminal Blocks Double Level | 3.4 | 3.4 | 340 |  | 2010-03-03 | 289237 / 10-P1267 | 400 | 2.07 | 828
200 | 1492-WTF3 | Terminal Blocks Triple Level | 5.05 | 5.05 | 1010 |  | 2010-03-03 | 289237 / 10-P1267 | 900 | 4.7 | 4230
20 | 1492-EB3 | End barrier for W4 | 0.6 | 0.6 | 12 |  | 2010-03-03 | 289237 / 10-P1267 | 50 | 0.6 | 30
30 | 1492-EA35 | End Anchor for W4 | 0.9 | 0.9 | 27 |  | 2010-03-03 | 289237 / 10-P1267 | 50 | 1.22 | 61
30 | 1492-GM35 | Terminal Group marker | 1.85 | 1.85 | 55.5 |  | 2010-03-03 | 289237 / 10-P1267 | 100 | 2.2 | 220
20 | 1492-EBD3 | End Barrier for WD3 | 1.01 | 1.01 | 20.2 |  | 2010-03-03 | 289237 / 10-P1267 | 200 | 0.77 | 154
30 | 1492-EAH35 | End Anchor for WD3 | 3.4 | 3.4 | 102 |  | 2010-03-03 | 289237 / 10-P1267 | 50 | 2.42 | 121
20 | 1492-EBFT3 | End Barrier for WTF3 | 1 | 1 | 20 |  | 2010-03-03 | 289237 / 10-P1267 | 50 | 0.97 | 48.5
15 | 1492-SJT5-20-B | JUMPERS 20-POLE PACAKGE OF 10 | 5.5 | 5.5 | 82.5 |  | 2010-03-03 | 289237 / 10-P1267 | 60 | 5.12 | 307.2
1 | 800T-H33B | KEYED SELECTOR SWITCH 2-POLE 2NO / 2NC | 133 | 133 | 133 |  | 2010-03-03 | 289237 / 10-P1267 | 6 | 87.15 | 522.9
11 | 800T-J91A | SWITCH 3-POSITION STC, 2NO, 2NC | 62 | 62 | 682 |  | 2010-03-03 | 289237 / 10-P1267 | 60 | 56.9 | 3414
1 | 700-ha33z24 | CONTROL RELAY 2PDT 24VDC 8-PIN | 13 | 13 | 13 |  | 2010-03-03 | 289237 / 10-P1267 | 6 | 12.37 | 74.22
1 | 700-HN126 | SOCKET FOR CONTROL RELAY | 7 | 7 | 7 |  | 2010-03-03 | 289237 / 10-P1267 | 6 | 5.76 | 34.56
2 | 1492-CB1G100 | CIRCUIT BREAKER 10 AMPS | 44 | 44 | 88 |  | 2010-03-03 | 289237 / 10-P1267 | 12 | 44.93 | 539.16
10 | 1492-CB1G050 | CIRCUIT BREAKER 5 AMPS | 44 | 44 | 440 |  | 2010-03-03 | 289237 / 10-P1267 | 6 | 44.93 | 269.58
10 | 1492-CB1G020 | CIRCUIT BREAKER 2 AMPS | 44 | 44 | 440 |  | 2010-03-03 | 289237 / 10-P1267 | 96 | 44.93 | 4313.28
10 | 199-DR1 | DIN MOUNTING RAIL | 6.3 | 6.3 | 63
10 | 885-2269 | BANANA JACK DOUBLE, BLACK | 2.4 | 2.4 | 24
1 | 90F7644 | RELAY TIMER | 84 | 84 | 84 |  | 2010-03-03 | 289237 / 10-P1267 | 6 | 173.91 | 1043.46
|  |  | Subtotal: |  | 4883.2 | 24416 |  |  |  |  | 17630.86
Connectors & hardware
30 | D2x4LKG6 | Wire Duct 2" x4" x 6ft length | 8 | 8 | 240
30 | C2LG6 | 2"x 4" Wire Duct cover 6ft length | 2 | 2 | 60
30 | D1.5x4LG6 | Wirer Duct 1.5'x4'x6ft length | 7.5 | 7.5 | 225 |  |  | Estimate of Various reqs for hardware |  |  | 4000
30 | C1.5LG6 | 1.5"x4" wire Duct cover 6ft length | 1.5 | 1.5 | 45
20 | 534-1301 | TERMINATION SUPPLIES, FERRULES, ETC | 50 | 50 | 1000
|  |  | Subtotal: |  | 1570 | 7850
Cables
1 | ALPHA 1736C/R1000 | CABLE 2 COND 22AWG 500 ft | 200 | 200 | 200 |  | 2012-07-12 | 319742/12-P1962-0 |  |  | 64396
7 | ALPHA 5470/25C | CABLE 25 COND 20AWG 500 ft | 4560 | 4560 | 31920 |  | 2013-01-24 | 326569/13-M0462 |  |  | 230
2 | ALPHA 45470/20C | CABLE 20COND 20 AWG 500 ft | 3125 | 3125 | 6250
|  | Rotation cable |  | 0 | 0 |  | 2013-03-08 | 326872 / 13-0532 |  |  | 3421.86
|  |  |  | 0 | 0 |  | 2010-07-13 | 293267 / 10-M2704-0 |  |  | 1145
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  | Subtotal: |  | 38370 | 191850 |  | Cables Ordered | 5 magnets |  | 69192.86
|  |  |  | Total | 47633.72 | 238168.6 |  |  |  | total | 90823.72 | -61.87%
Note on A57: FEET
Note on D32: :
Note on D42: POMONA 2269-0
Note on D43: CNT-35-96 TYCO ELECTRONICS
Note on D52: 22AWG FERRULES

## Instrumentation
| Instrumentation for all Magnets | Instrumentation for all Magnets |  |  | Date | PR/PO | Ordered | unit Cost | Total Cost
| 2007 prices and part number | 2010 part number | 2007 prices
qty | part # | Actual part # | unit cost | Total
12 | Honeywell FPG1BR,2P5B6A | OmegaDyne PX35D1-100GV | 565 | 6780 | 2010-03-09 | 289281 / 10-P1323 | 12 | 345.6 | 4147.2
6 | Edwards APG-M-NW16 | WRG-S-DN40CF Wide Range Vacuum Gauge | 230 | 1380 | 2010-03-09 | 289277 / 10-P1304 | 6 | 1123.2 | 6739.2
6 | Edwards AIM-X-DN40CF | (Combined gauge unit) | 560 | 3360 | 2010-03-09 | 289277 / 10-P1304 | 0 | 0 | 0
8 | Copper Nickel Alloy Film 120 Ohm GF=2.1 Half Bridge | (NOT NEEDED- PART OF MAGNET) |  |  |  | XXXXX
6 | Model 135 Monitor & Probe 80" | Model LM-500 with model 3DA sensor + cables | 3356 | 20136 | 2010-03-01 | 228063 /10-P1149 | 6 | 1762.5 | 10575
6 | Model 185 Ln2 level sensor and monitor | Model LM-500 with model LN2 sensor + cables | 2461 | 14766 | 2010-03-01 | 228063 /10-P1149 | 6 | 1845.8333 | 11075
12 | MKS MC20A00122LM26V | MCR-500SLPM-D_remote/5M,5IN,Gas:He | 3250 | 39000 | 2010-03-15 | 289247 / 10-P1271 | 10 | 2610 | 26100
4 | 3RTP100-2-2 Three axis Hall probe + accessories | XHGT-9060 | 804 | 3216 | 2013-03-08 | 326930 / CC | 4 | 813 | 3252
4 | Gauss meter | GM-700 | 1025 | 4100 | 2013-01-29 | 326752 / 13-P0475 | 4 | 1025 | 4100
6 | NMR probes+ cable (7M) | 1060-R-7m (R=3,4,5,6 & 7) 7 meter cable from amp to unit | 2700 | 16200 | 2013-01-07 | 326416 / 13-P0442 | 6 | 2777 | 16662
6 | Relay Board | ICC-ER-B24 | 224 | 1344 | 2010-03-08 | 289357 / 10-M13120 | 6 | 223.94 | 1343.64
10 | Constant Current Source Board | CMA1D03A | 80 | 800 | 2010-03-18 | 289256 / 10-P1310 | 10 | 370.27 | 3702.7
5 | Ball Valve Actuator (controller) | CE5-C-TX-HZ-G | 4000 | 20000 | 2010-04-30 | 289362 / 10-P1852 | 5 | 4094 | 20470
1 | UPS power protection | FJ000AAoAoAoAoB | 11000 | 11000 | 2013-07-10 | 332259 / 13-P1257 | 1 | 7137 | 7137
|  |  |  | 110282 |  |  |  |  | 115303.74 | 4.554%
Note on D5: Honeywell Web page http://www.sensotec.com/pressure_transducer_instock.shtml 3/7/07
Note on D6: From PR 191738 8/23/2000
Note on D7: From PR 191738 8/23/2000
Note on D9: American Magnetics Model 135 Monitor and sensor probe
Note on D10: American Magnetics
Note on D11: Flow Controllers PR# 255827 Model #1559A Calibrated to He gas 4-20mA output
Note on D13: GMW web page Pricing www.GMW.com
Note on D14: GMW web page Pricing www.GMW.com

## PRs
SHMS Electrical Components |  |  | 12CCMC | 12GEV | 43-014 & 43-053
PR | Sent Date | Due Date | PR Estimate | PO /Buyer | Vendor | PO Cost | Description | Delivery Complete | Location
288063 | 2010-01-21 | 2010-04-30 | 38300 | 10-P1149-0 /AD | Cryomagnetics | 21650 | Liquid Level Meters | 2010-05-10 | TED 1544
289228 | 2010-03-03 | 2010-03-31 | 25856 | 10-P1264-0 / AD | Macro Sensor | 27200 | LVDT cards | 2010-03-22 | TED 1544
289237 | 2010-03-03 | 2010-03-31 | 54884 | 10-P1266-0 / AD | Dataforth | 53328.5 | Signal Conditioners | 2010-04-29 | TED 1544
289247 | 2010-03-11 | 2010-03-31 | 26100 | 10-P1271-0 / AD | Alicat Scientific | 21280 | Flow meters | 2010-04-29 | TED 1544
289248 | 2010-03-05 | 2010-03-31 | 100965 | 10-P1267-0 / DL | EECO | 99996.56 | PLC parts | 2010-03-22 | TED 1544
289255 | 2010-03-03 | 2010-03-31 | 4680 | 10-P1249-0 / CP | Tiger Controls | 4062.24 | DC Power Supply | 2010-03-18 | TED 1544
289256 | 2010-03-04 | 2010-03-31 | 2830 | 10-M1310-0 / CP | 4PCB | 2956.4 | CC Board | 2010-04-08 | TED 1544
289277 | 2010-03-04 | 2010-03-31 | 6894 | 10-P1304-0 / CP | Tiger Controls | 6739.2 | Vacuum Gauges | 2010-04-12 | TED 1544
289281 | 2010-03-04 | 2010-03-31 | 4320 | 10-P1323-0 / CP | Omega | 4147.2 | Pressure Gauges | 2010-06-07 | TED 1544
289357 | 2010-03-08 | 2010-03-31 | 1344 | 10-M1312 / CP | ESI | 1343.64 | Relay Board | 2010-03-12 | TED 1544
289362 | 2010-03-25 | 2010-03-31 | 20000 | 10-P1852-0 / BR | Automax | 20470 | Warm Return Valve Actuator | 2010-07-26 | TED 1544
289430 | 2010-03-09 | 2010-03-31 | 800 | 10-P1310-0 / CP | 4PCB | 746.3 | CC Board LOI | 2010-04-08 | TED 1544
289485 | 2010-03-11 | 2010-03-31 | 3843.56 | 10-P0996-0/ BR | EECO | 3843.56 | PLC Chassis | 2010-03-25 | TED 1544
290013 | 2010-03-29 | 2010-03-31 | 4820 | 10-P1271-0 / AD | Alicat Scientific | 4820 | Flow meters LOI | 2010-04-29 | TED 1544
291622 | 2010-05-14 | 2010-06-02 | 4150 | 10-P2174-0 / CP | Tiger Controls | 4245 | I/O Modules | 2010-06-07 | TED 1544
293267 | 2010-07-07 | 2010-07-13 | 1666 | 10-M2704-0 | Tiger Controls | 1145 | Cables for Prototype Rack | 2010-07-16 | TED 1544
299653 | 2010-12-08 | 2011-01-14 | 1760 | 11-M0748 | Dataforth | 1650 | Signal Conditioners | 2011-01-14 | TED 1544
314004 | 2012-01-11 | 2012-02-07 | 6000 | 12-PO810 / TF | Prosoft | 6585 | ASCII Modules (PSU) + HW | 2012-01-31 | installed
314009 | 2012-01-11 | 2012-02-10 | 2038 | 12-M0772 | Dataforth | 2038 | HX Signal Conditioners | 2012-02-21 | TED 1544
314012 | 2012-01-11 | 2012-02-10 | 964 | 12-M0773 | Macro Sensors | 964 | LVDT Cards | 2012-01-23 | TED 1544
319742 | 2012-06-20 | 2012-10-26 | 230220 | 12-P1972 / AD | Tiger Controls | 64396 | cables (x6) [Local racks to I/O + magnet to I/O] | 2012-10-18 | ESB
326416 | 2013-01-07 | 2013-03-10 | 8000 | 13-PO442 / AD | Metro Lab | 16660 | NMR Probes x3 (Dipole) | 2013-03-20 | TED 1544
326569 | 2013-01-08 | 2013-02-08 | 2614 | 13-M0462 | EECO | 2614 | Ethernet Components | 2013-01-24 | TED 1544
326752 | 2013-01-15 | 2013-02-28 | N/A | 13-PO475 / KM | Cryo magnetics | 4100 | Gauss meters for hall probes | 2013-03-01 | installed
326834 | 2013-01-15 | 2013-01-25 | 620 | CREDITCARD/ CP | Dataforth | 635 | Signal Conditioners | 2013-01-25 | TED 1544
326872 | 2013-01-16 | 2013-03-08 | 4605.01 | 13-P0532 | Allied Electronics | 3421.86 | Rotation Cables | 2013-02-22 | ESB
326930 | 2013-01-18 | 2013-03-22 | 14740 | CREDITCARD/ CP | Lakeshore | 3251 | Hall Probes (HB,Q1,Q2,Q3) | 2013-03-22 | TED 1544
334996 | 2013-08-12 | 2013-09-27 | 14500 | 13-P1308 | EECO | 8440 | Software | 2013-08-30 | TED 1544
332259 | 2013-10-02 | 2013-11-29 | 11000 | 13-P1257 | Channel Corp | 7136.6 | 5.3 KVA Ferrite UPS | 2013-07-24 | TED 1544
337708 | 2013-10-29 | 2013-11-29 | 4800 |  | EECO |  | Hi speed I/O modules
[6 empty] | 4000 | connectors & hardware (x7) |  | TED 1544
|  |  | 603313.57 |  |  | 403865.06 | Total
[6 empty] | Label # | Racks Needed:
[6 empty] | 1 | HB | PLC 2nd floor CH
[6 empty] | 2 | Q1
[6 empty] | 3 | Q2
[6 empty] | 4 | Q3
[6 empty] | 5 | Dipole
[6 empty] | 6 | PSU/Quench Detectors/Cryogenics

## Chassis Layout
PLC I/O Usage Table
Magnets | [8 empty] | 8 Channels
Module | IV16 | OF4 | OW16I | OW16I | IF16 | IF16 | IF16 | IF16 | IF16
Configuration |  | 0-5 volts output |  |  | Single_Ended voltage | Single_Ended Voltage/Current | Single_Ended_Mode Voltage | Differential_Mode Current | Differential_Mode Voltage
Chasis Slot # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Channel
0 | QD_U1 | Setpnt_m_flow_LCL | MOT_JTV1_Close | He_CG_Current_enabled | TP_He_PT_1 | TR_Coil_1 | SG_1 | LVDT_JTV1 | Current Lead R
1 | QD_L1 | Setpnt_m_flow_RCL | MOT_JTV1_Open | Vacuum_power | TP_He_PT_2 | TR_Coil_2 | SG_2 | LVDT_JTV2 | Coil 1
2 | QD_U2 |  | MOT_JTV2_Close | Keep_Alive_Reset | TP_He_PT_3 | TR_Coil_3 | SG_3 | LVDT_JTV3 | Coil 2
3 | QD_L2 |  | MOT_JTV2_Open | Keep_Alive_Control | TP_He_PT_4 | TR_Coil_4 | SG_4 | LVDT_JTV4 | Coil 3
4 | QD_U3 |  | MOT_JTV3_Close | Power_liquid_level_meter | TP_LN2_OT | TR_He_LCLC | SG_5 | LVDT_JTV5 | Coil 4
5 | QD_L3 |  | MOT_JTV3_Open | PLC_Fast_Relay | TP_LN2_OB | TR_He_RCLC | SG_6 | LVDT_JTV6 | Current Lead L
6 | QD_U4 |  | MOT_JTV4_Close | PLC_Slow_Relay | TP_LN2_BT | TR_LHe_Resv | SG_7 | Warm_Return_Position | Coils 1 and 2
7 | QD_L4 |  | MOT_JTV4_Open | MPS_CPU_Reset | TP_LN2_BB |  | SG_8 | h_LHe / LN2 | Coils 3 and 4
8 | QD_Sum |  | MOT_JTV5_Close | MPS_diodes_Reset | TP_LN2_IN | Vac |  | N/A | N/A
9 | He_LL_alarm |  | MOT_JTV5_Open | Danf_QD_Reset | TP_LN2_Ret | p_He |  | N/A | N/A
10 | LN2_LL_alarm |  | MOT_JTV6-Close | He /LN2 LL select | TP_He_LCLW | p_N2 |  | N/A | N/A
11 | JVT Mtrs KS remote |  | MOT_JTV6_Open | Diode_Current_enabled | TP_He_RCLW | m_flow_LCL |  | N/A | N/A
12 | PSU_Control_pwr_on |  | Warm_return_Close |  | TD_LHe_CD | m_flow_RCL |  | N/A | N/A
13 | PSU_Main_pwr_on |  | Warm_return_Open |  | TD_LHe_Supply | MPS_Current_Signal |  | N/A | N/A
14 | PSU_ready |  |  |  | TD_LHe_Ret | Hall Probe |  | N/A | N/A
15 | PSU_Sum_Interlocks |  |  |  | TD_LHe_WR |  |  | N/A | N/A
Dataforth Signal Conditioner Table SCM5B modules
Rack
Channel |  |  |  |  | 3 | 1 | 5 |  | 6
1 |  |  | JT1 LN2 Cooldown |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
2 |  |  | JT2 LN2 Top Fill |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
3 |  |  | JT3 He Cooldown |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
4 |  |  | JT4 He Bottom Fill |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
5 |  |  | JT5 He Top Fill |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
6 |  |  | JT6 He Cold Return |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
7 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
8 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 30-07D [+/-1V to +/-10V] | 38-35D [+/-20mV - +/-10V] |  | 31-09D [+/-40V - +/-10V]
Channel |  |  |  |  | 2 | 4
1 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 31-03D [+/-10V - +/-10V]
2 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 38-35D [+/-20mV - +/-10V]
3 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 38-35D [+/-20mV - +/-10V]
4 |  |  |  |  | 34-1562 [RTD - +/- 5V] | 31-03D [+/-10V - +/-10V]
5 |  |  |  |  | 43-05D [+/-5V - +/-10V] | 31-03D [+/-10V - +/-10V]
6 |  |  |  |  | 43-05D [+/-5V - +/-10V] | 31-03D [+/-10V - +/-10V]
7 |  |  |  |  | 43-05D [+/-5V - +/-10V]
8 |  |  |  |  | 43-05D [+/-5V - +/-10V]