## Summary
Signal description | Range | Qty | Red Qty | Description |  | Magnet Interface Connector | Cable: Magnet to Rack | Signal Conditioner | I/O Signals to PLC | PLC I/O Module
|  |  |  | Internal sensors | Internal Cable
Temperature |  |  |  | Temperature sensors
Temperature Sensor N2 | > 60 K | 6 | 6 | PT100 3-wire LN2 | 12xBelden 9491 (One Triad) | B (50way) | Belden 1084A(8 triads) |  |  | 1756 - IR6I
Temperature Sensor CL | > 233K | 2 | 0 | PT100 3-wire Current Lead Top end | 2xBelden 9491 (One Triad) | C (15pin) | Belden 1084A(8 triads) |  |  | 1756 - IR6I
|  | 4 | 4 | PT100 3-wire Cool Down, Return, Cold massx2 | 8xBelden 9491 (One Triad) |  | Belden 1084A(8 triads) |  |  | 1756 - IR6I
|  | 2 | 2 | CG 3-wire Current Lead Top bottom | 4xBelden 9491 (One Triad) | A (50way) | Belden 1084A(8 triads) | Dataforth SCM5B34 - 1562 RTD Input | +/- 5 VDC | 1756 - IF16
Temperature Sensor He | > 60 K | 4 | 4 | CG 3-wire Coils | 2xBelden 9491 (One Triad) | C (15pin) | Belden 1084A(8 triads) | Dataforth SCM5B34 - 1562 RTD Input | +/- 5 VDC | 1756 - IF16
Temperature Sensor He | > 60 K | 3 | 2 | Diodes 2-wire Cooldown,Supply,Warm Return | 14xBelden 9491 (One Triad) | A (50way) | Belden 1084A(8 triads) | Dataforth SCM5B34 - 1562 RTD Input | +/- 5 VDC | 1756 - IF16
|  | 24 | 14 |  | 38 | Total #pins (A&B) = 96.0 | 5 | 24 (3 boards of 8 conditioners) |  | 2 X16 input modules single ended
Voltage Taps
|  | 4 | 2 | Curent Leads | AWG-24 wire HABIA cable AB | D (15pin) |  | SCM-5B31-09D | +/- 10 VDC | 1756 - IF16
|  | 4 | 4 | Coil to Coil Splices (Q1) | AWG-24 wire HABIA cable AB | D (15pin) |  | SCM-5B31-09D | +/- 10 VDC | 1756 - IF16
|  | 16 | 0 | Pancake Splices | AWG-24 wire HABIA cable AB |  |  | SCM-5B31-09D | +/- 10 VDC | 1756 - IF16
External sensors
Pressure |  |  |  | Pressure gauges
LN2 Pressure | 0.4 - 5 Bar | 1 | 0 | P6P/5bar Hottinger Baldwin Gmbh 5V/225Hz strain gauge full bridge | P 3-1 |  |  | Dataforth SCM5B38 - 35D | +/- 10 VDC | 1756 - IF16
LHe Pressure | 0.4 - 5 Bar | 1 | 0 | P6P/5bar Hottinger Baldwin Gmbh 5V/225Hz strain gauge full bridge | P 3-1 |  |  | Dataforth SCM5B38 - 35D | +/- 10 VDC | 1756 - IF16
Vacuum |  |  |  | Vacuum gauges
LH Thermovac TR206 | Vacuum gauge | 1 | 0 | 760 Torr to 1x10-3 Torr | P 3-3 |  |  | Leybold Combivac CM 31 | 0 - 10 VDC | 1756 - IF16
LH PenningVac PR 35 | Vacuum gauge | 1 | 0 | 1x10-2 Torr to 1x10-9 Torr | P 3-3 |  |  | Leybold Combivac CM 31 | 0 - 10 VDC | 1756 - IF16
Strain Gauges |  |  |  | Strain Guages
Gauge | 0 kN to 35 kN | 8 | 8 | CEA-06-125UT-350 Micro-measurement | P 4-1 |  |  | Dataforth SCM5B38 - 35D | +/- 10 VDC | 1756 - IF16
Liquid Level |  |  |  | Level Probes
LN2 Level | 0 - 100 % | 1 | 0 | Capitance 3 wire | P 6-1 |  |  | None | 4-20 mA
LHe Level | 0 - 100 % | 1 | 0 | Superconducting probe 4-wire | P 6-3 |  |  | Dataforth SCM5B31 - 03D | +/- 10 VDC | 1756 - IF16
Gas Flow Meters |  |  |  | Flow Meters
Lead He Gas Flow | 0-2000 sccm N2 | 2 |  | MKS 1749A-02000SV | P 7-1 |  |  | None | 4-20 mA | 1756 - IF16
JT Valves
JT Valve Manual/Auto Switch |  | 1 |  | Switch for all 11 JT valves | [5 empty] | 1756 - IB16D
Jt Valve Motors |  | 10 |  | Globe Motor (24 VDC @ 0.8A) | P 8-2 |  |  | Dataforth DSCA43-15C | 24V dc out to motor. | 1756 - OW16
LVDT | -6-100% | 10 |  | LVDT | P 8-1 |  |  | Macro Sensors LVC-2402 | 4-20 mA | 1756 - IF16
Magnet
Voltage Readings
Main Coil Voltages | +/- 500 VDC | 16 | 16 | AWG-28 wire HABIA cable AB | P 5-1 |  |  | Dataforth SCM5B31-090 | +/- 10 VDC | 1756 - IF16
NMR Unit |  |  |  | NMR
PLC commuications | Ascii | 1 |  | Metrolab Field Regulation RG2040 | P 9-1 |  |  | Flex I/O | RS232 | Control Net
Power on/off relay |  | 1 | [5 empty] | None |  | 1756 - OW16
Power Supply |  |  |  | PSU
PSU Interlocks and Status Signals |  | 16 |  | Interlock and Status Signals from PSU |  |  |  | None | Digital Signal | 1756 - IB16D
PSU Interlocks |  | 2 |  | Interlock Signals to the PSU from PLC |  |  |  | None |  | 1756 - OW16
PSU Reset Signal |  | 1 |  | Reset Signal to PSU & Diodes |  |  |  | None |  | 1756 - OW16
PSU Course Current Signal |  | 1 |  | 3 V dc +/- Dac output from PSU |  |  |  | Dataforth SCM5B31 - 03D | +/- 10 VDC | 1756 - IF16
Quench Detectors
Danfysik 4 Channel |  | 9 |  | Interlock Signals |  |  |  | None | Digital Signal | 1756 - IB16D
|  | 1 |  | Relay Contact |  |  |  | None
|  | 1 |  | Reset Signal |  |  |  | None |  | 1756 - OW16

## Signal List
Device | Range | ELIN's tag name | Device Connector | Cable Type | Connector | Cable | Wire | Term Strip | Pin | Wire | Signal | Pin | Pin | wire | Term Strip | Pin | PLC | Wire
Cryogenics |  |  | Signal/type/connector |  | Name | Pin | Color |  | Row-block | Color | Conditioner | In | Out | # |  | Row-block | Cable | # | location | Type | Tag Name
Temperature Sensor | >60K | T_LN2_1 | I+ | LiYCY18*.14 | M1T1 | 9 | sw | TS-10 | 2-1 | sw | SCM5B34-1562 | 3
PT100/1515 Ceramic |  | T_LN2_1 | I - | LiYCY18*.14 | M1T1 | 10 | vio | TS-10 | 3-1 | ge | RTD Input Module | 2
|  | T_LN2_1 | V+ | LiYCY18*.14 | M1T1 | 11 | gr-rs | TS-10 | 1-1 | sw | +/- 5Vdc | 4 | 1 | rt | TS-PLC-05 | 2-1 | 05 | TP-3 ws | 1:I:5:CH 2 + | 1756-IF16 | T_LN2_1
|  | T_LN2_1 | V - | LiYCY18*.14 | M1T1 | 12 | rt-bl | TS-10 | 4-1 | rt | 1-1 # 11346-1 | 1 | 3 | sw | TS-PLC-05 | 2-2 | 05 | TP-3 sw | 1:I:5:CH 2 -
|  | T_LN2_1r | I+ | LiYCY18*.14 | M1T1 | 13 | ws-gn | TS-10 | 2-2
|  | T_LN2_1r | I - | LiYCY18*.14 | M1T1 | 14 | br-gn | TS-10 | 3-2
|  | T_LN2_1r | V+ | LiYCY18*.14 | M1T1 | 15 | ws-ge | TS-10 | 1-2
|  | T_LN2_1r | V - | LiYCY18*.14 | M1T1 | 16 | ge-br | TS-10 | 4-2
|  | T_LN2_2 | I+ | LiYCY18*.14 | M2T2 | 9 | sw | TS-10 | 6-1 | sw | SCM5B34-1562 | 3
|  | T_LN2_2 | I - | LiYCY18*.14 | M2T2 | 10 | vio | TS-10 | 7-1 | or | RTD Input Module | 2
|  | T_LN2_2 | V+ | LiYCY18*.14 | M2T2 | 11 | gr-rs | TS-10 | 5-1 | sw | +/- 5Vdc | 4 | 5 | ws | TS-PLC-05 | 3-1 | 05 | TP-4 ws | 1:I:5:CH 3 + | 1756-IF16 | T_LN2_2
|  | T_LN2_2 | V - | LiYCY18*.14 | M2T2 | 12 | rt-bl | TS-10 | 8-1 | gn | 1-2 # 11346-2 | 1 | 6 | sw | TS-PLC-05 | 3-2 | 05 | TP-4 sw | 1:I:5:CH 3 -
|  | T_LN2_2r | I+ | LiYCY18*.14 | M2T2 | 13 | ws-gn | TS-10 | 6-2
|  | T_LN2_2r | I - | LiYCY18*.14 | M2T2 | 14 | br-gn | TS-10 | 7-2
|  | T_LN2_2r | V+ | LiYCY18*.14 | M2T2 | 15 | ws-ge | TS-10 | 5-2
|  | T_LN2_2r | V - | LiYCY18*.14 | M2T2 | 16 | ge-br | TS-10 | 8-2
|  | T_LN2_3 | I+ | LiYCY18*.14 | M3T3 | 9 | sw | TS-10 | 10-1 | sw | SCM5B34-1562 | 3
|  | T_LN2_3 | I - | LiYCY18*.14 | M3T3 | 10 | vio | TS-10 | 11-1 | bl | RTD Input Module | 2
|  | T_LN2_3 | V+ | LiYCY18*.14 | M3T3 | 11 | gr-rs | TS-10 | 9-1 | sw | +/- 5Vdc | 4 | 7 | gn | TS-PLC-05 | 5-1 | 05 | TP-5 ws | 1:I:5:CH 4 + | 1756-IF16 | T_LN2_3
|  | T_LN2_3 | V - | LiYCY18*.14 | M3T3 | 12 | rt-bl | TS-10 | 12-1 | ws | 1-3 # 11346-3 | 1 | 9 | sw | TS-PLC-05 | 5-2 | 05 | TP-5 sw | 1:I:5:CH 4 -
|  | T_LN2_3r | I+ | LiYCY18*.14 | M3T3 | 13 | ws-gn | TS-10 | 10-2
|  | T_LN2_3r | I - | LiYCY18*.14 | M3T3 | 14 | br-gn | TS-10 | 11-2
|  | T_LN2_3r | V+ | LiYCY18*.14 | M3T3 | 15 | ws-ge | TS-10 | 9-2
|  | T_LN2_3r | V - | LiYCY18*.14 | M3T3 | 16 | ge-br | TS-10 | 12-2
|  | T_LN2_4 | I+ | LiYCY18*.14 | M4T4 | 9 | sw | TS-10 | 14-1 | br | SCM5B34-1562 | 3
|  | T_LN2_4 | I - | LiYCY18*.14 | M4T4 | 10 | vio | TS-10 | 15-1 | rt | RTD Input Module | 2
|  | T_LN2_4 | V+ | LiYCY18*.14 | M4T4 | 11 | gr-rs | TS-10 | 13-1 | br | +/- 5Vdc | 4 | 11 | bl | TS-PLC-05 | 6-1 | 05 | TP-6 ws | 1:I:5:CH 5 + | 1756-IF16 | T_LN2_4
|  | T_LN2_4 | V - | LiYCY18*.14 | M4T4 | 12 | rt-bl | TS-10 | 16-1 | sw | 1-4 # 11346-4 | 1 | 12 | sw | TS-PLC-05 | 6-2 | 05 | TP-6 sw | 1:I:5:CH 5 -
|  | T_LN2_4r | I+ | LiYCY18*.14 | M4T4 | 13 | ws-gn | TS-10 | 14-2
|  | T_LN2_4r | I - | LiYCY18*.14 | M4T4 | 14 | br-gn | TS-10 | 15-2
|  | T_LN2_4r | V+ | LiYCY18*.14 | M4T4 | 15 | ws-ge | TS-10 | 13-2
|  | T_LN2_4r | V - | LiYCY18*.14 | M4T4 | 16 | ge-br | TS-10 | 16-2
|  | T_LN2_IN | I+ | LiYCY18*.14 | M4TIN | 9 | sw | TS-10 | 18-1 | gn | SCM5B34-1562 | 3
|  | T_LN2_IN | I - | LiYCY18*.14 | M4TIN | 10 | vio | TS-10 | 19-1 | br | RTD Input Module | 2
|  | T_LN2_IN | V+ | LiYCY18*.14 | M4TIN | 11 | gr-rs | TS-10 | 17-1 | gn | +/- 5Vdc | 4 | 13 | ge | TS-PLC-05 | 7-1 | 05 | TP-7 ws | 1:I:5:CH 6 + | 1756-IF16 | T_LN2_IN
|  | T_LN2_IN | V - | LiYCY18*.14 | M4TIN | 12 | rt-bl | TS-10 | 20-1 | rt | 1-5 # 11346-5 | 1 | 15 | sw | TS-PLC-05 | 7-2 | 05 | TP-7 sw | 1:I:5:CH 6 -
|  | T_LN2_INr | I+ | LiYCY18*.14 | M4TIN | 13 | ws-gn | TS-10 | 18-2
|  | T_LN2_INr | I - | LiYCY18*.14 | M4TIN | 14 | br-gn | TS-10 | 19-2
|  | T_LN2_INr | V+ | LiYCY18*.14 | M4TIN | 15 | ws-ge | TS-10 | 17-2
|  | T_LN2_INr | V - | LiYCY18*.14 | M4TIN | 16 | ge-br | TS-10 | 20-2
|  | T_LN2_OUT | I+ | LiYCY18*.14 | RTOUT | 9 | sw | TS-10 | 22-1 | gn | SCM5B34-1562 | 3
|  | T_LN2_OUT | I - | LiYCY18*.14 | RTOUT | 10 | vio | TS-10 | 23-1 | bl | RTD Input Module | 2
|  | T_LN2_OUT | V+ | LiYCY18*.14 | RTOUT | 11 | gr-rs | TS-10 | 21-1 | gn | +/- 5Vdc | 4 | 17 | br | TS-PLC-05 | 8-1 | 05 | TP-8 ws | 1:I:5:CH 7 + | 1756-IF16 | T_LN2_OUT
|  | T_LN2_OUT | V - | LiYCY18*.14 | RTOUT | 12 | rt-bl | TS-10 | 24-1 | or | 1-6 # 11346-6 | 1 | 18 | sw | TS-PLC-05 | 8-2 | 05 | TP-8 sw | 1:I:5:CH 7 -
|  | T_LN2_OUTr | I+ | LiYCY18*.14 | RTOUT | 13 | ws-gn | TS-10 | 22-2
|  | T_LN2_OUTr | I - | LiYCY18*.14 | RTOUT | 14 | br-gn | TS-10 | 23-2
|  | T_LN2_OUTr | V+ | LiYCY18*.14 | RTOUT | 15 | ws-ge | TS-10 | 21-2
|  | T_LN2_OUTr | V - | LiYCY18*.14 | RTOUT | 16 | ge-br | TS-10 | 24-2
Temperature Sensor | >233K | T_He_LCLW | I+ | LiYCY12x.14 | RTVCLW | 1 | ws | TS-10 | 26 | rt | SCM5B34-1562 | 3
PT 100/S65124B foil sensors |  | T_He_LCLW | I - | LiYCY12x.14 | RTVCLW | 2 | br | TS-10 | 27 | or | RTD Input Module | 2
|  | T_He_LCLW | V+ | LiYCY12x.14 | RTVCLW | 3 | gn | TS-10 | 25 | gn | +/- 5Vdc | 4 | 19 | or | TS-PLC-05 | 0-1 | 05 | TP-1 ws | 1:I:5:CH 0 + | 1756-IF16 | T_He_LCLW
|  | T_He_LCLW | V - | LiYCY12x.14 | RTVCLW | 4 | ge | TS-10 | 28 | ws | 1-8 # 11346-7 | 1 | 21 | sw | TS-PLC-05 | 0-2 | 05 | TP-1 sw | 1:I:5:CH 0 -
|  | T_He_RCLW | I+ | LiYCY12x.14 | RTVCLW | 5 | gr | TS-10 | 30 | rt | SCM5B34-1562 | 3
|  | T_He_RCLW | I - | LiYCY12x.14 | RTVCLW | 6 | rs | TS-10 | 31 | bl | RTD Input Module | 2
|  | T_He_RCLW | V+ | LiYCY12x.14 | RTVCLW | 7 | bl | TS-10 | 29 | rt | +/- 5Vdc | 4 | 23 | ws | TS-PLC-05 | 1-1 | 05 | TP-2 ws | 1:I:5:CH 1 + | 1756-IF16 | T_He_RCLW
|  | T_He_RCLW | V - | LiYCY12x.14 | RTVCLW | 8 | rt | TS-10 | 32 | ws | 1-7 # 11429-3 | 1 | 24 | rt | TS-PLC-05 | 1-2 | 05 | TP-2 sw | 1:I:5:CH 1 -
Temperature Sensor | < 60K | T_LHe_1 | I+ | LiYCY18*.14 | M1T1 | 1 | ws | TS-12 | 2-1 | rt | SCM5B31-03D
Thin Film Carbon Glass 4-wire |  | T_LHe_1 | I- | LiYCY18*.14 | M1T1 | 2 | br | TS-12 | 3-1 | sw | Volt input
|  | T_LHe_1 | V+ | LiYCY18*.14 | M1T1 | 3 | gn | TS-12 | 1-1 | sw | +/- 10VDC | 3 | 1 | rt | TS-PLC-05 | 9-1 | 05 | TP-9 ws | 1:I:5:CH 8 + | 1756-IF16 | T_LHe_1
|  | T_LHe_1 | V- | LiYCY18*.14 | M1T1 | 4 | ge | TS-12 | 4-1 | rt | 3-1 # 12661-1 | 2 | 3 | sw | TS-PLC-05 | 9-2 | 05 | TP-9 sw | 1:I:5:CH 8 -
|  | T_LHe_1r | I+ | LiYCY18*.14 | M1T1 | 5 | gr | TS-12 | 2-2
|  | T_LHe_1r | I- | LiYCY18*.14 | M1T1 | 6 | rs | TS-12 | 3-2
|  | T_LHe_1r | V+ | LiYCY18*.14 | M1T1 | 7 | bl | TS-12 | 1-2
|  | T_LHe_1r | V- | LiYCY18*.14 | M1T1 | 8 | rt | TS-12 | 4-2
|  | T_LHe_2 | I+ | LiYCY18*.14 | M2T2 | 1 | ws | TS-12 | 6-1 | ws | SCM5B31-03D
|  | T_LHe_2 | I- | LiYCY18*.14 | M2T2 | 2 | br | TS-12 | 7-1 | sw | Volt input
|  | T_LHe_2 | V+ | LiYCY18*.14 | M2T2 | 3 | gn | TS-12 | 5-1 | sw | +/- 10VDC | 3 | 5 | ws | TS-PLC-05 | 10-1 | 05 | TP-10 ws | 1:I:5:CH 9 + | 1756-IF16 | T_LHe_2
|  | T_LHe_2 | V- | LiYCY18*.14 | M2T2 | 4 | ge | TS-12 | 8-1 | ge | # 11346-8 | 2 | 6 | sw | TS-PLC-05 | 10-2 | 05 | TP-10 sw | 1:I:5:CH 9 -
|  | T_LHe_2r | I+ | LiYCY18*.14 | M2T2 | 5 | gr | TS-12 | 6-2 |  | 3-2 # 12661-2
|  | T_LHe_2r | I- | LiYCY18*.14 | M2T2 | 6 | rs | TS-12 | 7-2
|  | T_LHe_2r | V+ | LiYCY18*.14 | M2T2 | 7 | bl | TS-12 | 5-2
|  | T_LHe_2r | V- | LiYCY18*.14 | M2T2 | 8 | rt | TS-12 | 8-2
|  | T_LHe_3 | I+ | LiYCY18*.14 | M3T3 | 1 | ws | TS-12 | 10-1 | gn | SCM5B31-03D
|  | T_LHe_3 | I- | LiYCY18*.14 | M3T3 | 2 | br | TS-12 | 11-1 | sw | Volt input
|  | T_LHe_3 | V+ | LiYCY18*.14 | M3T3 | 3 | gn | TS-12 | 9-1 | sw | +/- 10VDC | 3 | 7 | gn | TS-PLC-05 | 11-1 | 05 | TP-11 ws | 1:I:5:CH 10 + | 1756-IF16 | T_LHe_3
|  | T_LHe_3 | V- | LiYCY18*.14 | M3T3 | 4 | ge | TS-12 | 12-1 | gn | # 11346-9 | 2 | 9 | sw | TS-PLC-05 | 11-2 | 05 | TP-11 sw | 1:I:5:CH 10 -
|  | T_LHe_3r | I+ | LiYCY18*.14 | M3T3 | 5 | gr | TS-12 | 10-2 |  | 3-3 # 12661-3
|  | T_LHe_3r | I- | LiYCY18*.14 | M3T3 | 6 | rs | TS-12 | 11-2
|  | T_LHe_3r | V+ | LiYCY18*.14 | M3T3 | 7 | bl | TS-12 | 9-2
|  | T_LHe_3r | V- | LiYCY18*.14 | M3T3 | 8 | rt | TS-12 | 12-2
|  | T_LHe_4 | I+ | LiYCY18*.14 | M4T4 | 1 | ws | TS-12 | 14-1 | bl | SCM5B31-03D
|  | T_LHe_4 | I- | LiYCY18*.14 | M4T4 | 2 | br | TS-12 | 15-1 | sw | Volt input
|  | T_LHe_4 | V+ | LiYCY18*.14 | M4T4 | 3 | gn | TS-12 | 13-1 | sw | +/- 10VDC | 3 | 11 | bl | TS-PLC-05 | 12-1 | 05 | TP-12 ws | 1:I:5:CH 11 + | 1756-IF16 | T_LHe_4
|  | T_LHe_4 | V- | LiYCY18*.14 | M4T4 | 4 | ge | TS-12 | 16-1 | or | 3-4 #12661-4 | 2 | 12 | sw | TS-PLC-05 | 12-2 | 05 | TP-12 sw | 1:I:5:CH 11 -
|  | T_LHe_4r | I+ | LiYCY18*.14 | M4T4 | 5 | gr | TS-12 | 14-2
|  | T_LHe_4r | I- | LiYCY18*.14 | M4T4 | 6 | rs | TS-12 | 15-2
|  | T_LHe_4r | V+ | LiYCY18*.14 | M4T4 | 7 | bl | TS-12 | 13-2
|  | T_LHe_4r | V- | LiYCY18*.14 | M4T4 | 8 | rt | TS-12 | 16-2
|  | T_LHe_IN | I+ | LiYCY18*.14 | M4TIN | 1 | ws | TS-12 | 18-1 | ge | SCM5B31-03D
|  | T_LHe_IN | I- | LiYCY18*.14 | M4TIN | 2 | br | TS-12 | 19-1 | sw | Volt input
|  | T_LHe_IN | V+ | LiYCY18*.14 | M4TIN | 3 | gn | TS-12 | 17-1 | sw | +/- 10VDC | 3 | 13 | ge | TS-PLC-05 | 14-1 | 05 | TP-13 ws | 1:I:5:CH 12 + | 1756-IF16 | T_LHe_In
|  | T_LHe_IN | V- | LiYCY18*.14 | M4TIN | 4 | ge | TS-12 | 20-1 | ws | 3-5 # 12661-5 | 2 | 15 | sw | TS-PLC-05 | 14-2 | 05 | TP-13 sw | 1:I:5:CH 12 -
|  | T_LHe_INr | I+ | LiYCY18*.14 | M4TIN | 5 | gr | TS-12 | 18-2
|  | T_LHe_INr | I- | LiYCY18*.14 | M4TIN | 6 | rs | TS-12 | 19-2
|  | T_LHe_INr | V+ | LiYCY18*.14 | M4TIN | 7 | bl | TS-12 | 17-2
|  | T_LHe_INr | V- | LiYCY18*.14 | M4TIN | 8 | rt | TS-12 | 20-2
|  | T_LHe_OUT | I+ | LiYCY18*.14 | RTOUT | 1 | ws | TS-12 | 22-1 | br | SCM5B31-03D
|  | T_LHe_OUT | I- | LiYCY18*.14 | RTOUT | 2 | br | TS-12 | 23-1 | sw | Volt input
|  | T_LHe_OUT | V+ | LiYCY18*.14 | RTOUT | 3 | gn | TS-12 | 21-1 | sw | +/- 10VDC | 3 | 17 | br | TS-PLC-05 | 15-1 | 05 | TP-14 ws | 1:I:5:CH 13 + | 1756-IF16 | T_LHe_Out
|  | T_LHe_OUT | V- | LiYCY18*.14 | RTOUT | 4 | ge | TS-12 | 24-1 | bl | 3-6 # 12661-6 | 2 | 18 | sw | TS-PLC-05 | 15-2 | 05 | TP-14 sw | 1:I:5:CH 13 -
|  | T_LHe_OUTr | I+ | LiYCY18*.14 | RTOUT | 5 | gr | TS-12 | 22-2
|  | T_LHe_OUTr | I- | LiYCY18*.14 | RTOUT | 6 | rs | TS-12 | 23-2
|  | T_LHe_OUTr | V+ | LiYCY18*.14 | RTOUT | 7 | bl | TS-12 | 21-2
|  | T_LHe_OUTr | V- | LiYCY18*.14 | RTOUT | 8 | rt | TS-12 | 24-2
|  | T_Lhe_LCLC | I+ | LiYCY18*.14 | RTCLC | 1 | ws | TS-12 | 26-1 | or | SCM5B31-03D
|  | T_Lhe_LCLC | I- | LiYCY18*.14 | RTCLC | 2 | br | TS-12 | 27-1 | sw | Volt input
|  | T_Lhe_LCLC | V+ | LiYCY18*.14 | RTCLC | 3 | gn | TS-12 | 25-1 | sw | +/- 10VDC | 3 | 19 | or | TS-PLC-05 | 16-1 | 05 | TP-15 ws | 1:I:5:CH 14 + | 1756-IF16 | T_LHe_LCLC
|  | T_Lhe_LCLC | V- | LiYCY18*.14 | RTCLC | 4 | ge | TS-12 | 28-1 | br | 3-7 #12661-7 | 2 | 21 | sw | TS-PLC-05 | 16-2 | 05 | TP-15 sw | 1:I:5:CH 14 -
|  | T_Lhe_LCLCr | I+ | LiYCY18*.14 | RTCLC | 5 | gr | TS-12 | 26-2
|  | T_Lhe_LCLCr | I- | LiYCY18*.14 | RTCLC | 6 | rs | TS-12 | 27-2
|  | T_Lhe_LCLCr | V+ | LiYCY18*.14 | RTCLC | 7 | bl | TS-12 | 25-2
|  | T_Lhe_LCLCr | V- | LiYCY18*.14 | RTCLC | 8 | rt | TS-12 | 28-2
|  | T_Lhe_RCLC | I+ | LiYCY18*.14 | RTCLC | 9 | sw | TS-12 | 30-1 | ws | SCM5B31-03D
|  | T_Lhe_RCLC | I- | LiYCY18*.14 | RTCLC | 10 | vio | TS-12 | 31-1 | rt | Volt input
|  | T_Lhe_RCLC | V+ | LiYCY18*.14 | RTCLC | 11 | gr-rs | TS-12 | 29-1 | rt | +/- 10VDC | 3 | 23 | ws | TS-PLC-05 | 17-1 | 05 | TP-16 ws | 1:I:5:CH 15 + | 1756-IF16 | T_LHe_RCLC
|  | T_Lhe_RCLC | V- | LiYCY18*.14 | RTCLC | 12 | rt-bl | TS-12 | 32-1 | ws | 3-8 # 12604-1 | 2 | 24 | rt | TS-PLC-05 | 17-2 | 05 | TP-16 sw | 1:I:5:CH 15 -
|  | T_Lhe_RCLCr | I+ | LiYCY18*.14 | RTCLC | 13 | ws-gn | TS-12 | 30-2
|  | T_Lhe_RCLCr | I- | LiYCY18*.14 | RTCLC | 14 | br-gn | TS-12 | 31-2
|  | T_Lhe_RCLCr | V+ | LiYCY18*.14 | RTCLC | 15 | ws-ge | TS-12 | 29-2
|  | T_Lhe_RCLCr | V- | LiYCY18*.14 | RTCLC | 16 | ge-br | TS-12 | 32-2
Current Lead (CL) Gas Flow Controllers / Meters
+Lead He Gas Flow | 0-2000sccm N2 | m_flow_LCL | V+ | LiYCY 7*.14 | RFLCL | 7 | ws | TS-20 | 4-1 | [5 empty] | TS-PLC-06 | 0-2 | 06
MKS 1749A - 02000SV +24Vdc input 4-20 mA output |  | m_flow_LCL | M+ | LiYCY 7*.14 | RFLCL | 2 | br | TS-20 | 3-1 | [5 empty] | TS-PLC-06 | 0-2 | 06
|  | m_flow_LCL | M- | LiYCY 7*.14 | RFLCL | 9 | gn | TS-20 | 1-1 | [5 empty] | TS-PLC-06 | 0-1 | 06 | TP-1 | 1:I:6:CH 0 + | 1756-IF16 | m_flow_LCL
|  | m_flow_LCL | V- | LiYCY 7*.14 | RFLCL | 5 | ge | TS-20 | 2-1 | [5 empty] | TS-PLC-06 | 0-3 | 06 | TP-1 | 1:I:6:CH 0 -
|  |  | Chasis Gnd | LiYCY 7*.14 | RFLCL | 15 | S | TS-20 | SH
-Lead He Gas Flow |  | m_flow_RCL | V+ | LiYCY 7*.14 | RFRCL | 7 | ws | TS-20 | 8-1 | [5 empty] | TS-PLC-06 | 1-2 | 06
MKS 1749A - 02000SV +24Vdc input 4-20 mA output |  | m_flow_RCL | M+ | LiYCY 7*.14 | RFRCL | 2 | br | TS-20 | 7-1 | [5 empty] | TS-PLC-06 | 1-2 | 06
|  | m_flow_RCL | M- | LiYCY 7*.14 | RFRCL | 9 | gn | TS-20 | 5-1 | [5 empty] | TS-PLC-06 | 1-1 | 06 | TP-2 | 1:I:6:CH 1 + | 1756-IF16 | m_flow_RCL
|  | m_flow_RCL | V- | LiYCY 7*.14 | RFRCL | 5 | ge | TS-20 | 6-1 | [5 empty] | TS-PLC-06 | 1-3 | 06 | TP-2 | 1:I:6:CH 1 -
|  |  | Chasis Gnd | LiYCY 7*.14 | RFRCL | 15 | S | TS-20 | SH
HX He Temp | 300-73K | T_HX_he | I+ | CEBAF | DTHE | 1 | br | TS-11 | 2-1 |  | SCM5B34-1562 | 3
Pt-100 |  | T_HX_he | I - | CEBAF | DTHE | 2 | rt | TS-11 | 3-1 |  | RTD Input Module | 2
|  | T_HX_he | V+ | CEBAF | DTHE | 3 | gn | TS-11 | 1-1 |  | +/- 5Vdc | 4 | 1 | rt | TS_PLC_07 | 0-1 | 07 | TP-1 ws | 1:I:7:CH 0 + | 1756-IF16 | T_Hx_He
|  | T_HX_he | V - | CEBAF | DTHE | 4 | bl | TS-11 | 4-1 |  | 2-1 # 11429-1 | 1 | 3 | sw | TS_PLC_07 | 0-2 | 07 | TP-1 sw | 1:I:7:CH 0 -
HX N2 Temp | 300-73K | T_HX_n2 | I+ | CEBAF | DTHE | 1 | br | TS-11 | 6-1 |  | SCM5B34-1562 | 3
PT-100 |  | T_HX_n2 | I - | CEBAF | DTHE | 2 | rt | TS-11 | 7-1 |  | RTD Input Module | 2
|  | T_HX_n2 | V+ | CEBAF | DTHE | 3 | gn | TS-11 | 5-1 |  | +/- 5Vdc | 4 | 5 | ws | TS_PLC_07 | 12-1 | 07 | TP-13 ws | 1:I:7:CH 11 + | 1756-IF16 | T_Hx_N2
|  | T_HX_n2 | V - | CEBAF | DTHE | 4 | bl | TS-11 | 8-1 |  | 2-2 # 11429-2 | 1 | 6 | sw | TS_PLC_07 | 12-2 | 07 | TP-13 sw | 1:I:7:CH 11 -
Vacuum
LH Thermovac TR206 | Vacuum gauge | Thermo_X |  | 1*.75 |  | 31 | bl | TS-17 | 3 | [5 empty] | TS_PLC_06 | 14-1 | 06 | TP-15 | 1:I:6:CH 12 + | 1756-IF16 | Thermo_x
760 Torr to 1 * 10^-3 |  |  |  | 1*.75 |  | 32 | sw | TS-17 | 4 | [5 empty] | TS_PLC_06 | 14-2 | 06 | TP-15 | 1:I:6:CH 12 -
LH PenningVac PR 35 | Vacuum gauge | Penning_X |  | 1*.75 |  | 231 | bl | TS-17 | 12 | [5 empty] | TS_PLC_06 | 15-1 | 06 | TP-16 | 1:I:6:CH 13 + | 1756-IF16 | Penning_x
|  |  |  | 1*.75 |  | 232 | sw | TS-17 | 13 | [5 empty] | TS_PLC_06 | 15-2 | 06 | TP-16 | 1:I:6:CH 13 -
[6 empty] | 233 |  | TS-17 | 9 | [5 empty] | TS_PLC_04 | 6-1 | 04 | o,gn | 1:O:4:07 out | 1756-OW16 | Penning_HV
[6 empty] | 211 |  | TS-17 | 10 | [5 empty] | TS_PLC_04 | 6-2 | 04 | o,bk,gn | 1:O:4:07 in
[6 empty] | 212 |  | TS-17 | 11 | [5 empty] | TS_PLC_04 | 6-3 | 04 |  | 110130
Pressure
LN2 Pressure | 0.4 - 4 bar | p_N2 | 1 | LiYCY 6*0.14 | RPN2 | V | ws | TS-13 | 5 | sw | SCM5B38-35D | 4 | 5 | ws | TS_PLC_06 | 12-1 | 06 | TP-13 ws | 1:I:6:CH 11 + | 1756-IF16 | p_N2
P6P/5bar |  | p_N2 | 2 | LiYCY 6*0.14 | RPN2 | X | br | TS-13 | 6 | sw | Voltage Input | 3
Full Bridge |  | p_N2 | 3 | LiYCY 6*0.14 | RPN2 | U | gn | TS-13 | 7 | or | +/- 10 VDC | 2
|  | p_N2 | 4 | LiYCY 6*0.14 | RPN2 | W | ge | TS-13 | 8 | gn | 4-2 # 11380-10 | 1 | 6 | sw | TS_PLC_06 | 12-2 | 06 | TP-13 sw | 1:I:6:CH 11 -
|  | p_N2 | 2' | LiYCY 6*0.14 | RPN2 | X | gr | TS-13 | 6
|  | p_N2 | 3' | LiYCY 6*0.14 | RPN2 | U | rs | TS-13 | 7
|  |  |  | LiYCY 6*0.14 |  |  | S | TS-13 | SH
LHe Pressure | 0.4 - 4 bar | p_He | 1 | LiYCY 6*0.14 | RPHE | V | ws | TS-13 | 1 | sw | SCM5B38-35D | 4 | 1 | rt | TS_PLC_06 | 11-1 | 06 | TP-12 ws | 1:I:6:CH 10 + | 1756-IF16 | p_He
P6P/5bar |  | p_He | 2 | LiYCY 6*0.14 | RPHE | X | br | TS-13 | 2 | sw | Voltage Input | 3
Full Bridge |  | p_He | 3 | LiYCY 6*0.14 | RPHE | U | gn | TS-13 | 3 | ge | +/- 10 VDC | 2
|  | p_He | 4 | LiYCY 6*0.14 | RPHE | W | ge | TS-13 | 4 | rt | 4-1 # 11380-9 | 1 | 3 | sw | TS_PLC_06 | 11-2 | 06 | TP-12 sw | 1:I:6:CH 10 -
|  | p_He | 2' | LiYCY 6*0.14 | RPHE | X | gr | TS-13 | 2
|  | p_He | 3' | LiYCY 6*0.14 | RPHE | U | rs | TS-13 | 3
|  |  |  | LiYCY 6*0.14 |  |  | S | TS-13 | SH
Liquid Level
LN2 Level | 0-100% | h_LN2 |  | LiYCY 3*0.14 | RLLN2 |  | ws | TS-19 | 1-1 | [5 empty] | TS_PLC_06 | 5-2 | 06
|  | h_LN2 |  | LiYCY 3*0.14 | RLLN2 |  | br | TS-19 | 2-1 | [5 empty] | TS_PLC_06 | 5-1 | 06 | TP-6 | 1:I:6:CH 4 + | 1756-IF16 | h_LN2
|  | h_LN2 |  | LiYCY 3*0.14 | RLLN2 |  | gn | TS-19 | 3-1 | [5 empty] | TS_PLC_06 | 5-3 | 06 | TP-6 | 1:I:6:CH 4 -
S
Lhe | 0-100% | h_LHe | I+ | LiYCY 6*0.14 | RLLHE | 1 | ws | TS-13 | 10 | rt | SCM5B31-03D
|  | h_LHe | V+ | LiYCY 6*0.14 | RLLHE | 2 | br | TS-13 | 9 | sw | Voltage Input | 3 | 7 | gn | TS_PLC_06 | 17-1 | 06 | TP-18 ws | 1:I:6:CH 15 + | 1756-IF16 | h_Lhe
|  | h_LHe | V- | LiYCY 6*0.14 | RLLHE | 3 | gn | TS-13 | 12 | ws | +/- 40 VDC | 2 | 9 | sw | TS_PLC_06 | 17-2 | 06 | TP-18 sw | 1:I:6:CH 15 -
|  | h_LHe | I- | LiYCY 6*0.14 | RLLHE | 4 | ge | TS-13 | 11 | sw | 4-3 #
Warm Return Temperature | 300-73 K
PT 100 DIN 23760
|  |  |  | LiYCY 6*0.14 |  |  | S | TS-13 | SH
JT Valves
LHE Magnet | -6-100% | MOT_JTV1 | C+ | YSLV 4*.5 | RJTV1M | C | ws | TS-22 | 0-1
Globe Motor(24 VDC @0.8 A) |  | MOT_JTV1 | O- | YSLV 4*.5 | RJTV1M | D | br | TS-22 | 1-2
|  | MOT_JTV1 | O+ | YSLV 4*.5 | RJTV1M | F | gn | TS-22 | 1-1
|  | MOT_JTV1 | C- | YSLV 4*.5 | RJTV1M | G | ge | TS-22 | 0-2
Cooldown Control | -6-100% | MOT_JTV2 | C+ | YSLV 4*.5 | RJTV2M | C | ws | TS-22 | 2-1
|  | MOT_JTV2 | O- | YSLV 4*.5 | RJTV2M | D | br | TS-22 | 3-2
|  | MOT_JTV2 | O+ | YSLV 4*.5 | RJTV2M | F | gn | TS-22 | 3-1
|  | MOT_JTV2 | C- | YSLV 4*.5 | RJTV2M | G | ge | TS-22 | 2-2
LN2 magnet | -6-100% | MOT_JTV3 | C+ | YSLV 4*.5 | RJTV3M | C | ge | TS-22 | 4-1
Globe Motor(24 VDC @0.8 A) |  | MOT_JTV3 | O- | YSLV 4*.5 | RJTV3M | D | ws | TS-22 | 5-2
|  | MOT_JTV3 | O+ | YSLV 4*.5 | RJTV3M | F | br | TS-22 | 5-1
|  | MOT_JTV3 | C- | YSLV 4*.5 | RJTV3M | G | gn | TS-22 | 4-2
LN2 Reservoir | -6-100% | MOT_JTV4 | C+ | YSLV 4*.5 | RJTV4M | C | ge | TS-22 | 6-1
Globe Motor(24 VDC @0.8 A) |  | MOT_JTV4 | O- | YSLV 4*.5 | RJTV4M | D | ws | TS-22 | 7-2
|  | MOT_JTV4 | O+ | YSLV 4*.5 | RJTV4M | F | br | TS-22 | 7-1
|  | MOT_JTV4 | C- | YSLV 4*.5 | RJTV4M | G | gn | TS-22 | 6-2
LHE Reservoir | -6-100% | MOT_JTV5 | C+ | YSLV 4*.5 | RJTV5M | C | ws | TS-22 | 8-1
Globe Motor(24 VDC @0.8 A) |  | MOT_JTV5 | O- | YSLV 4*.5 | RJTV5M | D | sw | TS-22 | 9-2
|  | MOT_JTV5 | O+ | YSLV 4*.5 | RJTV5M | F | gn | TS-22 | 9-1
|  | MOT_JTV5 | C- | YSLV 4*.5 | RJTV5M | G | rt | TS-22 | 8-2
LHE Return | -6-100% | MOT_JTV6 | C+ | YSLV 4*.5 | RJTV6M | C | ws | TS-22 | 10-1
Globe Motor(24 VDC @0.8 A) |  | MOT_JTV6 | O- | YSLV 4*.5 | RJTV6M | D | br | TS-22 | 11-2
|  | MOT_JTV6 | O+ | YSLV 4*.5 | RJTV6M | F | gn | TS-22 | 11-1
|  | MOT_JTV6 | C- | YSLV 4*.5 | RJTV6M | G | ge | TS-22 | 10-2
CL Gas Flow's JT Valve |  | MOT_JTV7 | C+ | OE-OZ 4*.5 | RJTV7M | C | ws | TS-22 | 12-1
Globe Motor(24 VDC @0.8 A) |  | MOT_JTV7 | O- | OE-OZ 4*.5 | RJTV7M | D | sw | TS-22 | 13-2
|  | MOT_JTV7 | O+ | OE-OZ 4*.5 | RJTV7M | F | gn | TS-22 | 13-1
|  | MOT_JTV7 | C- | OE-OZ 4*.5 | RJTV7M | G | rt | TS-22 | 12-2
|  | MOT_JTV8 | C+ | YSLY 4*.5 | RJTV8M | C | sw1 | TS-22 | 14-1
|  | MOT_JTV8 | O- | YSLY 4*.5 | RJTV8M | D | sw2 | TS-22 | 15-2
|  | MOT_JTV8 | O+ | YSLY 4*.5 | RJTV8M | F | sw3 | TS-22 | 15-1
|  | MOT_JTV8 | C- | YSLY 4*.5 | RJTV8M | G | sw4 | TS-22 | 14-2
HX Helium JT Valve |  | MOT_JTV9 | C+ | YSLY 4*.5 | RJTV9M | C | ws | TS-22 | 16-1
|  | MOT_JTV9 | O- | YSLY 4*.5 | RJTV9M | D | sw | TS-22 | 17-2
|  | MOT_JTV9 | O+ | YSLY 4*.5 | RJTV9M | F | gn | TS-22 | 17-1
|  | MOT_JTV9 | C- | YSLY 4*.5 | RJTV9M | G | rt | TS-22 | 16-2
HX Nitrogen JT Valve |  | MOT_JTV10 |  | YSLY 4*.5 | RJTV9M | C | ws | TS-22 | 18-1
|  | MOT_JTV10 |  | YSLY 4*.5 | RJTV9M | D | sw | TS-22 | 19-2
|  | MOT_JTV10 |  | YSLY 4*.5 | RJTV9M | F | gn | TS-22 | 19-1
|  | MOT_JTV10 |  | YSLY 4*.5 | RJTV9M | G | rt | TS-22 | 18-2
Warm Return |  | Close | C+ |  |  |  |  | TS-22 | 20-1
Automax (24VDC @ 0.8 A) |  | Open | O- |  |  |  |  | TS-22 | 21-2
|  | Open | O+ |  |  |  |  | TS-22 | 21-1
|  | Close | C- |  |  |  |  | TS-22 | 20-2
| 4-20mA | Postion
JT LVDT's |  | LVDT_JTV1 | A | LiYCY 5 * .14 | RJTV1L |  | ws |  |  |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 1-1 | 07 | TP-2 | 1:I:7:CH 1 + | 1756-IF16 | LVDT_JT1
|  | LVDT_JTV1 | D | LiYCY 5 * .14 | RJTV1L |  | sw |  |  |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 1-2 | 07 | TP-2 | 1:I:7:CH 1 -
|  | LVDT_JTV1 | E | LiYCY 5 * .14 | RJTV1L |  | ge |  |  |  |  | 8
|  | LVDT_JTV1 | F | LiYCY 5 * .14 | RJTV1L |  | br |  |  |  |  | 11
|  | LVDT_JTV1 | B/C | LiYCY 5 * .14 | RJTV1L |  | rs/gn
|  | LVDT_JTV1 | S | LiYCY 5 * .14 | RJTV1L |  | sw
|  | LVDT_JTV2 | A | LiYCY 5 * .14 | RJTV2L |  | ws |  |  |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 2-1 | 07 | TP-3 | 1:I:7:CH 2 + | 1756-IF16 | LVDT_JT2
|  | LVDT_JTV2 | D | LiYCY 5 * .14 | RJTV2L |  | sw |  |  |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 2-2 | 07 | TP-3 | 1:I:7:CH 2 -
|  | LVDT_JTV2 | E | LiYCY 5 * .14 | RJTV2L |  | ge |  |  |  |  | 8
|  | LVDT_JTV2 | F | LiYCY 5 * .14 | RJTV2L |  | br |  |  |  |  | 11
|  | LVDT_JTV1 | B/C | LiYCY 5 * .14 | RJTV1L |  | rs/gn
|  | LVDT_JTV2 | S | LiYCY 5 * .14 | RJTV2L |  | sw
|  | LVDT_JTV3 | A | LiYCY 5 * .14 | RJTV3L |  | ws |  |  |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 3-1 | 07 | TP-4 | 1:I:7:CH 3 + | 1756-IF16 | LVDT_JT3
|  | LVDT_JTV3 | D | LiYCY 5 * .14 | RJTV3L |  | sw |  |  |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 3-2 | 07 | TP-4 | 1:I:7:CH 3 -
|  | LVDT_JTV3 | E | LiYCY 5 * .14 | RJTV3L |  | ge |  |  |  |  | 8
|  | LVDT_JTV3 | F | LiYCY 5 * .14 | RJTV3L |  | br |  |  |  |  | 11
|  | LVDT_JTV1 | B/C | LiYCY 5 * .14 | RJTV1L |  | rs/gn
|  | LVDT_JTV3 | S | LiYCY 5 * .14 | RJTV3L |  | sw
|  | LVDT_JTV4 | A | LiYCY 5 * .14 | RJTV4L |  | ws |  |  |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 5-1 | 07 | TP-6 | 1:I:7:CH 4 + | 1756-IF16 | LVDT_JT4
|  | LVDT_JTV4 | D | LiYCY 5 * .14 | RJTV4L |  | sw |  |  |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 5-2 | 07 | TP-6 | 1:I:7:CH 4 -
|  | LVDT_JTV4 | E | LiYCY 5 * .14 | RJTV4L |  | ge |  |  |  |  | 8
|  | LVDT_JTV4 | F | LiYCY 5 * .14 | RJTV4L |  | br |  |  |  |  | 11
|  | LVDT_JTV1 | B/C | LiYCY 5 * .14 | RJTV1L |  | rs/gn
|  | LVDT_JTV4 | S | LiYCY 5 * .14 | RJTV4L |  | sw
|  | LVDT_JTV5 | A | LiYCY 5 * .14 | RJTV5L |  | ws |  |  |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 6-1 | 07 | TP-7 | 1:I:7:CH 5 + | 1756-IF16 | LVDT_JT5
|  | LVDT_JTV5 | D | LiYCY 5 * .14 | RJTV5L |  | sw |  |  |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 6-2 | 07 | TP-7 | 1:I:7:CH 5 -
|  | LVDT_JTV5 | E | LiYCY 5 * .14 | RJTV5L |  | ge |  |  |  |  | 8
|  | LVDT_JTV5 | F | LiYCY 5 * .14 | RJTV5L |  | br |  |  |  |  | 11
|  | LVDT_JTV1 | B/C | LiYCY 5 * .14 | RJTV1L |  | rs/gn
|  | LVDT_JTV5 | S | LiYCY 5 * .14 | RJTV5L |  | sw
|  | LVDT_JTV6 | A | LiYCY 5 * .14 | RJTV6L |  | ws |  |  |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 7-1 | 07 | TP-8 | 1:I:7:CH 6 + | 1756-IF16 | LVDT_JT6
|  | LVDT_JTV6 | D | LiYCY 5 * .14 | RJTV6L |  | sw |  |  |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 7-2 | 07 | TP-8 | 1:I:7:CH 6 -
|  | LVDT_JTV6 | E | LiYCY 5 * .14 | RJTV6L |  | ge |  |  |  |  | 8
|  | LVDT_JTV6 | F | LiYCY 5 * .14 | RJTV6L |  | br |  |  |  |  | 11
|  | LVDT_JTV1 | B/C | LiYCY 5 * .14 | RJTV1L |  | rs/gn
|  | LVDT_JTV6 | S | LiYCY 5 * .14 | RJTV6L |  | sw
CL Gas Flow's JT valve LVDT | -6-100% | LVDT_JTV7 | A | LiYCY 5*.14 | RJTV7L |  | ws |  |  |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 8-1 | 07 | TP-9 | 1:I:7:CH 7 + | 1756-IF16 | LVDT_JT7
Existing |  | LVDT_JTV7 | D | LiYCY 5*.14 | RJTV7L |  | rt |  |  |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 8-2 | 07 | TP-9 | 1:I:7:CH 7 -
|  | LVDT_JTV7 | E | LiYCY 5*.14 | RJTV7L |  | bl |  |  |  |  | 8
|  | LVDT_JTV7 | F | LiYCY 5*.14 | RJTV7L |  | br |  |  |  |  | 11
|  | LVDT_JTV1 | B/C | LiYCY 5 * .14 | RJTV1L |  | rs/gn
|  | LVDT_JTV7 | S | LiYCY 5*.14 | RJTV7L |  | sw
|  | LVDT_JTV8 | A | LiYCY 5*.14 | RJTV8L |  | ws |  |  |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 9-1 | 07 | TP-10 | 1:I:7:CH 8 + | 1756-IF16 | LVDT_JT8
|  | LVDT_JTV8 | D | LiYCY 5*.14 | RJTV8L |  | gr |  |  |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 9-2 | 07 | TP-10 | 1:I:7:CH 8 -
|  | LVDT_JTV8 | E | LiYCY 5*.14 | RJTV8L |  | ge |  |  |  |  | 8
|  | LVDT_JTV8 | F | LiYCY 5*.14 | RJTV8L |  | br |  |  |  |  | 11
|  | LVDT_JTV1 | B/C | LiYCY 5 * .14 | RJTV1L |  | rs/gn
|  | LVDT_JTV8 | S | LiYCY 5*.14 | RJTV8L |  | sw
HX He JT LVDT | -6-100% | LVDT_JTV9 | rt | LiYCY 5*.14 | RJTV9L | A | rt | TS-21 | 1-1 |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 10-1 | 07 | TP-11 | 1:I:7:CH 9 + | 1756-IF16 | LVDT_JT9
|  | LVDT_JTV9 | sw | LiYCY 5*.14 | RJTV9L | D | sw | TS-21 | 2-1 |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 10-2 | 07 | TP-11 | 1:I:7:CH 9 -
|  | LVDT_JTV9 | ge | LiYCY 5*.14 | RJTV9L | E | gn | TS-21 | 3-1 |  |  | 8
|  | LVDT_JTV9 | br | LiYCY 5*.14 | RJTV9L | F | bl | TS-21 | 4-1 |  |  | 11
|  | LVDT_JTV9 |  |  |  |  | S | TS-21 | SH
HX N2 JT LVDT | -6-100% | LVDT_JTV10 | A | LiYCY 5*.14 | RJTV9L |  | rt | TS-21 | 5-1 |  | MacroSensor | 9 | 5 |  | TS_PLC_07 | 11-1 | 07 | TP-12 | 1:I:7:CH 10 + | 1756-IF16 | LVDT_JT10
|  | LVDT_JTV10 | D | LiYCY 5*.14 | RJTV9L |  | sw | TS-21 | 6-1 |  | LVC-2402 | 7 | 6 |  | TS_PLC_07 | 11-2 | 07 | TP-12 | 1:I:7:CH 10 -
|  | LVDT_JTV10 | E | LiYCY 5*.14 | RJTV9L |  | gn | TS-21 | 7-1 |  |  | 8
|  | LVDT_JTV10 | F | LiYCY 5*.14 | RJTV9L |  | bl | TS-21 | 8-1 |  |  | 11
|  | LVDT_JTV10 |  | LiYCY 5*.14 |  |  | S |  | SH
Strain Gauges
Gauge | 0 KN to 35 KN | F_R1 | X1 | LiYCY 12 * .14 | M1SGR | 1 | ws | TS-14 | 1-1 | sw | SCMB38-35D | 4
CEA-06-125UT-350 Micro Measurement |  | F_R1 | X2 | LiYCY 12 * .14 | M1SGR | 2 | br | TS-14 | 2-1 | sw | FULL BRIDGE | 3 | 1 | rt | TS-PLC-08 | 9-1 | 08 | TP-10 ws | 1:I:8:CH 8 + | 1756-IF16 | F_R1
|  | F_R1 | X3 | LiYCY 12 * .14 | M1SGR | 3 | gn | TS-14 | 3-1 | ge | +/- 5V Output | 2 | 3 | sw | TS-PLC-08 | 9-2 |  | TP-10 sw | 1:I:8:CH 8 -
|  | F_R1 | X4 | LiYCY 12 * .14 | M1SGR | 4 | ge | TS-14 | 4-1 | rt | 5-1 #11380-11 | 1
|  | F_R1 | X2' | LiYCY 12 * .14 | M1SGR | 5 | gr | TS-14 | 5-1
|  | F_R1 | X3' | LiYCY 12 * .14 | M1SGR | 6 | rs | TS-14 | 6-1
|  | F_R1r | X2' | LiYCY 12 * .14 | M1SGR | 9 | bl | TS-14 | 5-2
|  | F_R1r | X3' | LiYCY 12 * .14 | M1SGR | 10 | rt | TS-14 | 6-2
|  | F_R1r | X1 | LiYCY 12 * .14 | M1SGR | 11 | sw | TS-14 | 1-2
|  | F_R1r | X2 | LiYCY 12 * .14 | M1SGR | 12 | vio | TS-14 | 2-2
|  | F_R1r | X3 | LiYCY 12 * .14 | M1SGR | 7 | gr-rs | TS-14 | 3-2
|  | F_R1r | X4 | LiYCY 12 * .14 | M1SGR | 8 | rt-bl | TS-14 | 4-2
[7 empty] | S | TS-14 | SH
|  | F_L1 | X1 | LiYCY 12 * .14 | M1SGL | 1 | ws | TS-14 | 25-1 | gn | SCMB38-35D | 4
|  | F_L1 | X2 | LiYCY 12 * .14 | M1SGL | 2 | br | TS-14 | 26-1 | gn | FULL BRIDGE | 3 | 13 | ge | TS-PLC-08 | 10-1 | 08 | TP-11 ws | 1:I:8:CH 9 + | 1756-IF16 | F_L1
|  | F_L1 | X3 | LiYCY 12 * .14 | M1SGL | 3 | gn | TS-14 | 27-1 | br | +/- 5V Output | 2 | 15 | sw | TS-PLC-08 | 10-2 |  | TP-11 sw | 1:I:8:CH 9 -
|  | F_L1 | X4 | LiYCY 12 * .14 | M1SGL | 4 | ge | TS-14 | 28-1 | rt | 5-5 #11380-5 | 1
|  | F_L1 | X2' | LiYCY 12 * .14 | M1SGL | 5 | gr | TS-14 | 29-1
|  | F_L1 | X3' | LiYCY 12 * .14 | M1SGL | 6 | rs | TS-14 | 30-1
|  | F_L1r | X2' | LiYCY 12 * .14 | M1SGL | 9 | bl | TS-14 | 29-2
|  | F_L1r | X3' | LiYCY 12 * .14 | M1SGL | 10 | rt | TS-14 | 30-2
|  | F_L1r | X1 | LiYCY 12 * .14 | M1SGL | 11 | sw | TS-14 | 25-2
|  | F_L1r | X2 | LiYCY 12 * .14 | M1SGL | 12 | vio | TS-14 | 26-2
|  | F_L1r | X3 | LiYCY 12 * .14 | M1SGL | 7 | gr-rs | TS-14 | 27-2
|  | F_L1r | X4 | LiYCY 12 * .14 | M1SGL | 8 | rt-bl | TS-14 | 28-2
[7 empty] | S | TS-14 | SH
|  | F_R2 | X1 | LiYCY 12 * .14 | M2SGR | 1 | ws | TS-14 | 7-1 | sw | SCMB38-35D | 4
|  | F_R2 | X2 | LiYCY 12 * .14 | M2SGR | 2 | br | TS-14 | 8-1 | sw | FULL BRIDGE | 3 | 5 | ws | TS-PLC-08 | 11-1 | 08 | TP-12 ws | 1:I:8:CH 10 + | 1756-IF16 | F_R2
|  | F_R2 | X3 | LiYCY 12 * .14 | M2SGR | 3 | gn | TS-14 | 9-1 | or | +/- 5V Output | 2 | 6 | sw | TS-PLC-08 | 11-2 |  | TP-12 sw | 1:I:8:CH 10 -
|  | F_R2 | X4 | LiYCY 12 * .14 | M2SGR | 4 | ge | TS-14 | 10-1 | gn | 5-2 #11380-12 | 1
|  | F_R2 | X2' | LiYCY 12 * .14 | M2SGR | 5 | gr | TS-14 | 11-1
|  | F_R2 | X3' | LiYCY 12 * .14 | M2SGR | 6 | rs | TS-14 | 12-1
|  | F_R2r | X2' | LiYCY 12 * .14 | M2SGR | 9 | bl | TS-14 | 11-2
|  | F_R2r | X3' | LiYCY 12 * .14 | M2SGR | 10 | rt | TS-14 | 12-2
|  | F_R2r | X1 | LiYCY 12 * .14 | M2SGR | 11 | sw | TS-14 | 7-2
|  | F_R2r | X2 | LiYCY 12 * .14 | M2SGR | 12 | vio | TS-14 | 8-2
|  | F_R2r | X3 | LiYCY 12 * .14 | M2SGR | 7 | gr-rs | TS-14 | 9-2
|  | F_R2r | X4 | LiYCY 12 * .14 | M2SGR | 8 | rt-bl | TS-14 | 10-2
[7 empty] | S | TS-14 | SH
|  | F_L2 | X1 | LiYCY 12 * .14 | M2SGL | 1 | ws | TS-14 | 31-1 | gn | SCMB38-35D | 4
|  | F_L2 | X2 | LiYCY 12 * .14 | M2SGL | 2 | br | TS-14 | 32-1 | gn | FULL BRIDGE | 3 | 17 | br | TS-PLC-08 | 12-1 | 08 | TP-13 ws | 1:I:8:CH 11 + | 1756-IF16 | F_L2
|  | F_L2 | X3 | LiYCY 12 * .14 | M2SGL | 3 | gn | TS-14 | 33-1 | bl | +/- 5V Output | 2 | 18 | sw | TS-PLC-08 | 12-2 |  | TP-13 sw | 1:I:8:CH 11 -
|  | F_L2 | X4 | LiYCY 12 * .14 | M2SGL | 4 | ge | TS-14 | 34-1 | or | 5-6 #11380-6 | 1
|  | F_L2 | X2' | LiYCY 12 * .14 | M2SGL | 5 | gr | TS-14 | 35-1
|  | F_L2 | X3' | LiYCY 12 * .14 | M2SGL | 6 | rs | TS-14 | 36-1
|  | F_L2r | X2' | LiYCY 12 * .14 | M2SGL | 9 | bl | TS-14 | 35-2
|  | F_L2r | X3' | LiYCY 12 * .14 | M2SGL | 10 | rt | TS-14 | 36-2
|  | F_L2r | X1 | LiYCY 12 * .14 | M2SGL | 11 | sw | TS-14 | 31-2
|  | F_L2r | X2 | LiYCY 12 * .14 | M2SGL | 12 | vio | TS-14 | 32-2
|  | F_L2r | X3 | LiYCY 12 * .14 | M2SGL | 7 | gr-rs | TS-14 | 33-2
|  | F_L2r | X4 | LiYCY 12 * .14 | M2SGL | 8 | rt-bl | TS-14 | 34-2
[7 empty] | S | TS-14 | SH
Strain Gauges |  | F_R3 | X1 | LiYCY 12 * .14 | M3SGR | 1 | ws | TS-14 | 13-1 | sw | SCMB38-35D | 4
Gauge | 0 KN to 35 KN | F_R3 | X2 | LiYCY 12 * .14 | M3SGR | 2 | br | TS-14 | 14-1 | sw | FULL BRIDGE | 3 | 7 | gn | TS-PLC-08 | 14-1 | 08 | TP-14 ws | 1:I:8:CH 12 + | 1756-IF16 | F_R3
CEA-06-125UT-350 Micro Measurement |  | F_R3 | X3 | LiYCY 12 * .14 | M3SGR | 3 | gn | TS-14 | 15-1 | bl | +/- 5V Output | 2 | 9 | sw | TS-PLC-08 | 14-2 |  | TP-14 sw | 1:I:8:CH 12 -
|  | F_R3 | X4 | LiYCY 12 * .14 | M3SGR | 4 | ge | TS-14 | 16-1 | ws | 5-3 #11380-3 | 1
|  | F_R3 | X2' | LiYCY 12 * .14 | M3SGR | 5 | gr | TS-14 | 17-1
|  | F_R3 | X3' | LiYCY 12 * .14 | M3SGR | 6 | rs | TS-14 | 18-1
|  | F_R3r | X2' | LiYCY 12 * .14 | M3SGR | 9 | bl | TS-14 | 17-2
|  | F_R3r | X3' | LiYCY 12 * .14 | M3SGR | 10 | rt | TS-14 | 18-2
|  | F_R3r | X1 | LiYCY 12 * .14 | M3SGR | 11 | sw | TS-14 | 13-2
|  | F_R3r | X2 | LiYCY 12 * .14 | M3SGR | 12 | vio | TS-14 | 14-2
|  | F_R3r | X3 | LiYCY 12 * .14 | M3SGR | 7 | gr-rs | TS-14 | 15-2
|  | F_R3r | X4 | LiYCY 12 * .14 | M3SGR | 8 | rt-bl | TS-14 | 16-2
[7 empty] | S | TS-14 | SH
|  | F_L3 | X1 | LiYCY 12 * .14 | M3SGL | 1 | ws | TS-14 | 37-1 | gn | SCMB38-35D | 4
|  | F_L3 | X2 | LiYCY 12 * .14 | M3SGL | 2 | br | TS-14 | 38-1 | rt | FULL BRIDGE | 3 | 19 | or | TS-PLC-08 | 15-1 | 08 | TP-15 ws | 1:I:8:CH 13 + | 1756-IF16 | F_L3
|  | F_L3 | X3 | LiYCY 12 * .14 | M3SGL | 3 | gn | TS-14 | 39-1 | or | +/- 5V Output | 2 | 21 | sw | TS-PLC-08 | 15-2 |  | TP-15 sw | 1:I:8:CH 13 -
|  | F_L3 | X4 | LiYCY 12 * .14 | M3SGL | 4 | ge | TS-14 | 40-1 | ws | 5-7 #11380-7 | 1
|  | F_L3 | X2' | LiYCY 12 * .14 | M3SGL | 5 | gr | TS-14 | 41-1
|  | F_L3 | X3' | LiYCY 12 * .14 | M3SGL | 6 | rs | TS-14 | 42-1
|  | F_L3r | X2' | LiYCY 12 * .14 | M3SGL | 9 | bl | TS-14 | 41-2
|  | F_L3r | X3' | LiYCY 12 * .14 | M3SGL | 10 | rt | TS-14 | 42-2
|  | F_L3r | X1 | LiYCY 12 * .14 | M3SGL | 11 | sw | TS-14 | 37-2
|  | F_L3r | X2 | LiYCY 12 * .14 | M3SGL | 12 | vio | TS-14 | 38-2
|  | F_L3r | X3 | LiYCY 12 * .14 | M3SGL | 7 | gr-rs | TS-14 | 39-2
|  | F_L3r | X4 | LiYCY 12 * .14 | M3SGL | 8 | rt-bl | TS-14 | 40-2
[7 empty] | S | TS-14 | SH
|  | F_R4 | X1 | LiYCY 12 * .14 | M4SGR | 1 | ws | TS-14 | 19-1 | br | SCMB38-35D | 4
|  | F_R4 | X2 | LiYCY 12 * .14 | M4SGR | 2 | br | TS-14 | 20-1 | br | FULL BRIDGE | 3 | 11 | bl | TS-PLC-08 | 16-1 | 08 | TP-16 ws | 1:I:8:CH 14 + | 1756-IF16 | F_R4
|  | F_R4 | X3 | LiYCY 12 * .14 | M4SGR | 3 | gn | TS-14 | 21-1 | rt | +/- 5V Output | 2 | 12 | sw | TS-PLC-08 | 16-2 |  | TP-16 sw | 1:I:8:CH 14 -
|  | F_R4 | X4 | LiYCY 12 * .14 | M4SGR | 4 | ge | TS-14 | 22-1 | sw | 5-4 #11380-4 | 1
|  | F_R4 | X2' | LiYCY 12 * .14 | M4SGR | 5 | gr | TS-14 | 23-1
|  | F_R4 | X3' | LiYCY 12 * .14 | M4SGR | 6 | rs | TS-14 | 24-1
|  | F_R4r | X2' | LiYCY 12 * .14 | M4SGR | 9 | bl | TS-14 | 23-2
|  | F_R4r | X3' | LiYCY 12 * .14 | M4SGR | 10 | rt | TS-14 | 24-2
|  | F_R4r | X1 | LiYCY 12 * .14 | M4SGR | 11 | sw | TS-14 | 19-2
|  | F_R4r | X2 | LiYCY 12 * .14 | M4SGR | 12 | vio | TS-14 | 20-2
|  | F_R4r | X3 | LiYCY 12 * .14 | M4SGR | 7 | gr-rs | TS-14 | 21-2
|  | F_R4r | X4 | LiYCY 12 * .14 | M4SGR | 8 | rt-bl | TS-14 | 22-2
[7 empty] | S | TS-14 | SH
|  | F_L4 | X1 | LiYCY 12 * .14 | M4SGL | 1 | ws | TS-14 | 43-1 | rt | SCMB38-35D | 4
|  | F_L4 | X2 | LiYCY 12 * .14 | M4SGL | 2 | br | TS-14 | 44-1 | rt | FULL BRIDGE | 3 | 23 | ws | TS-PLC-08 | 17-1 | 08 | TP-17 ws | 1:I:8:CH 15 + | 1756-IF16 | F_L4
|  | F_L4 | X3 | LiYCY 12 * .14 | M4SGL | 3 | gn | TS-14 | 45-1 | bl | +/- 5V Output | 2 | 24 | rt | TS-PLC-08 | 17-2 |  | TP-17 sw | 1:I:8:CH 15 -
|  | F_L4 | X4 | LiYCY 12 * .14 | M4SGL | 4 | ge | TS-14 | 46-1 | ws | 5-8 #11380-8 | 1
|  | F_L4 | X2' | LiYCY 12 * .14 | M4SGL | 5 | gr | TS-14 | 47-1
|  | F_L4 | X3' | LiYCY 12 * .14 | M4SGL | 6 | rs | TS-14 | 48-1
|  | F_L4r | X2' | LiYCY 12 * .14 | M4SGL | 9 | bl | TS-14 | 47-2
|  | F_L4r | X3' | LiYCY 12 * .14 | M4SGL | 10 | rt | TS-14 | 48-2
|  | F_L4r | X1 | LiYCY 12 * .14 | M4SGL | 11 | sw | TS-14 | 43-2
|  | F_L4r | X2 | LiYCY 12 * .14 | M4SGL | 12 | vio | TS-14 | 44-2
|  | F_L4r | X3 | LiYCY 12 * .14 | M4SGL | 7 | gr-rs | TS-14 | 45-2
|  | F_L4r | X4 | LiYCY 12 * .14 | M4SGL | 8 | rt-bl | TS-14 | 46-2
[7 empty] | S | TS-14 | SH
Magnet
Voltage Readings
Main Coil Voltages & Current Leads | +/- 500 VDC | [9 empty] | SCM-5B31-09D
AWG-24 wire HABIA cable AB |  | VT_1_a | V | LiYCY2x24x.14 | RVT | 1 | ws | TS-15 | 1-2 | sw | 6-1 #11411-1 | 3 | 1 | rt | TS-PLC-09 | 0-1 | 09 | TP-1 | 1:I:9:CH 0 + | 1756-IF16 | U_1
|  | VT_2_a | V | LiYCY2x24x.14 | RVT | 2 | br | TS-15 | 2-2 | ge | 6-1 #11411-1 | 2 | 3 | sw | TS-PLC-09 | 1-1 | 09 | TP-2 | 1:I:9:CH 0 - | 1756-IF16
Wired to PLC Input and |  | VT_3_a | V | LiYCY2x24x.14 | RVT | 3 | gn | TS-15 | 3-2 | sw | 6-2 #11411-2 | 3 | 5 | ws | TS-PLC-09 | 2-1 | 09 | TP-3 | 1:I:9:CH 1 + | 1756-IF16 | U_2
to Danfysik Quench Detector |  | VT_4_a | V | LiYCY2x24x.14 | RVT | 4 | ge | TS-15 | 4-2 | or | 6-2 #11411-2 | 2 | 6 | sw | TS-PLC-09 | 3-1 | 09 | TP-4 | 1:I:9:CH 1 - | 1756-IF16
see hw05-1.doc Page 5-7 Fig 5.4 |  | VT_5_a | V | LiYCY2x24x.14 | RVT | 5 | gr | TS-15 | 5-2 | sw | 6-3 #11411-3 | 3 | 7 | gn | TS-PLC-09 | 5-1 | 09 | TP-6 | 1:I:9:CH 2 + | 1756-IF16 | U_3
|  | VT_6_a | V | LiYCY2x24x.14 | RVT | 6 | rs | TS-15 | 6-2 | bl | 6-3 #11411-3 | 2 | 9 | sw | TS-PLC-09 | 6-1 | 09 | TP-7 | 1:I:9:CH 2 - | 1756-IF16
|  | VT_7_a | V | LiYCY2x24x.14 | RVT | 7 | bl | TS-15 | 7-2 | sw | 6-4 #11411-11 | 3 | 11 | bl | TS-PLC-09 | 7-1 | 09 | TP-8 | 1:I:9:CH 3 + | 1756-IF16 | U_4
|  | VT_8_a | V | LiYCY2x24x.14 | RVT | 8 | rt | TS-15 | 8-2 | rt | 6-4 #11411-11 | 2 | 12 | sw | TS-PLC-09 | 8-1 | 09 | TP-9 | 1:I:9:CH 3 - | 1756-IF16
|  | VT_9_a | V | LiYCY2x24x.14 | RVT | 9 | sw | TS-15 | 9-2 | sw | 6-5 #11411-12 | 3 | 13 | ge | TS-PLC-09 | 9-1 | 09 | TP-10 | 1:I:9:CH 4 + | 1756-IF16 | U_5
|  | VT_10_a | V | LiYCY2x24x.14 | RVT | 10 | vio | TS-15 | 10-2 | gn | 6-5 #11411-12 | 2 | 15 | sw | TS-PLC-09 | 10-1 | 09 | TP-11 | 1:I:9:CH 4 - | 1756-IF16
|  | VT_11_a | V | LiYCY2x24x.14 | RVT | 11 | gr-rs | TS-15 | 11-2 | sw | 6-6 #11411-6 | 3 | 17 | br | TS-PLC-09 | 11-1 | 09 | TP-12 | 1:I:9:CH 5 + | 1756-IF16 | U_6
|  | VT_12_a | V | LiYCY2x24x.14 | RVT | 12 | rt-bl | TS-15 | 12-2 | br | 6-6 #11411-6 | 2 | 18 | sw | TS-PLC-09 | 12-1 | 09 | TP-13 | 1:I:9:CH 5 - | 1756-IF16
|  | VT_13_a | V | LiYCY2x24x.14 | RVT | 13 | ws-gn | TS-15 | 13-2 | ws | 671 #11411-7 | 3 | 19 | or | TS-PLC-09 | 14-1 | 09 | TP-15 | 1:I:9:CH 6 + | 1756-IF16 | U_7
|  | VT_14_a | V | LiYCY2x24x.14 | RVT | 14 | br-gn | TS-15 | 14-2 | rt | 671 #11411-7 | 2 | 21 | sw | TS-PLC-09 | 15-1 | 09 | TP-16 | 1:I:9:CH 6 - | 1756-IF16
|  | VT_15_a | V | LiYCY2x24x.14 | RVT | 15 | ws-ge | TS-15 | 15-2 | sw | 6-8 #11411-8 | 3 | 23 | ws | TS-PLC-09 | 16-1 | 09 | TP-17 | 1:I:9:CH 7 + | 1756-IF16 | U_8
|  | VT_16_a | V | LiYCY2x24x.14 | RVT | 16 | ge-br | TS-15 | 16-2 | ws | 6-8 #11411-8 | 2 | 24 | rt | TS-PLC-09 | 17-1 | 09 | TP-18 | 1:I:9:CH 7- | 1756-IF16
|  |  |  | LiYCY2x24x.14 |  |  | S | TS-15
|  | VT_1_b | V | LiYCY2x24x.14 | RVT | 17 | wr-gr | TS-15 | 1-1 |  | TB-18 | 1 & 3 |  | rt,ws | QD 1 | d1h,d1lm
|  | VT_2_b | V | LiYCY2x24x.14 | RVT | 18 | gr-br | TS-15 | 2-1 |  | TB-18 | 2 & 4 |  | sw,sw | QD 1 | d1hm,d1l
|  | VT_3_b | V | LiYCY2x24x.14 | RVT | 19 | ws-rs | TS-15 | 3-1
|  | VT_4_b | V | LiYCY2x24x.14 | RVT | 20 | rs-br | TS-15 | 4-1
|  | VT_5_b | V | LiYCY2x24x.14 | RVT | 21 | ws-bl | TS-15 | 5-1
|  | VT_6_b | V | LiYCY2x24x.14 | RVT | 22 | br-bl | TS-15 | 6-1
|  | VT_7_b | V | LiYCY2x24x.14 | RVT | 23 | ws-rt | TS-15 | 7-1
|  | VT_8_b | V | LiYCY2x24x.14 | RVT | 24 | br-rt | TS-15 | 8-1
|  | VT_9_b | V | LiYCY2x24x.14 | RVT | 25 | ws-sw | TS-15 | 9-1
|  | VT_10_b | V | LiYCY2x24x.14 | RVT | 26 | br-sw | TS-15 | 10-1
|  | VT_11_b | V | LiYCY2x24x.14 | RVT | 27 | gr-gn | TS-15 | 11-1
|  | VT_12_b | V | LiYCY2x24x.14 | RVT | 28 | ge-gr | TS-15 | 12-1
|  | VT_13_b | V | LiYCY2x24x.14 | RVT | 29 | rs-gn | TS-15 | 13-1
|  | VT_14_b | V | LiYCY2x24x.14 | RVT | 30 | ge-rs | TS-15 | 14-1
|  | VT_15_b | V | LiYCY2x24x.14 | RVT | 31 | gn-bl | TS-15 | 15-1 |  | TB-18 | 9 & 11 |  | ge, br | QD 3 | d3h,d3lm
|  | VT_16_b | V | LiYCY2x24x.14 | RVT | 32 | ge-bl | TS-15 | 16-1 |  | TB-18 | 10 & 12 |  | sw, sw | QD 3 | d3hm,d3l
|  | VL | V | LiYCY2x24x.14 | RVT | 33 | ws | TS-15 | 17-1 |  | TB-18 | 5 |  | gn | QD 2 | d2h
|  | VM | V | LiYCY2x24x.14 | RVT | 34 | br | TS-15 | 17-2 |  | TB-18 | 6 |  | sw | QD 2 | d2hm
|  | VM | V | LiYCY2x24x.14 | RVT | 34 | gn | TS-15 | 18-1 |  | TB-18 | 7 |  | bl | QD 2 | d2lm
|  | VR | V | LiYCY2x24x.14 | RVT | 35 | ge | TS-15 | 18-2 |  | TB-18 | 8 |  | sw | QD 2 | d2lm
Quench Detector
Status Outputs |  | U1 |  |  |  | 1 | rt |  |  |  | TB-18 | 17 | rt |  | TS_PLC_01 | 0-1 | 01 | 1w | 1:I:1:00 | 1756-IV16 | U1
Connector P5 |  | L1 |  |  |  | 2 | sw |  |  |  | TB-18 | 18 | sw |  | TS_PLC_01 | 1-1 | 01 | 1b | 1:I:1:01 | 1756-IV16 | L1
|  | U2 |  |  |  | 3 | ws |  |  |  | TB-18 | 19 | ws |  | TS_PLC_01 | 2-1 | 01 | 2w | 1:I:1:02 | 1756-IV16 | U2
|  | L2 |  |  |  | 4 | sw |  |  |  | TB-18 | 20 | bl |  | TS_PLC_01 | 3-1 | 01 | 2b | 1:I:1:03 | 1756-IV16 | L2
|  | U3 |  |  |  | 5 | gn |  |  |  | TB-18 | 21 | gn |  | TS_PLC_01 | 4-1 | 01 | 3w | 1:I:1:04 | 1756-IV16 | U3
|  | L3 |  |  |  | 6 | sw |  |  |  | TB-18 | 22 | or |  | TS_PLC_01 | 5-1 | 01 | 3b | 1:I:1:05 | 1756-IV16 | L3
|  | U4 |  |  |  | 7 | bl |  |  |  | TB-18 | 23 | br |  | TS_PLC_01 | 6-1 | 01 | 4w | 1:I:1:06 | 1756-IV16 | U4
|  | L4 |  |  |  | 8 | sw |  |  |  | TB-18 | 24 | ge |  | TS_PLC_01 | 7-1 | 01 | 4b | 1:I:1:07 | 1756-IV16 | L4
|  | SUM |  |  |  | 9 | ge |  |  |  | TB-18 | 25 | gr |  | TS_PLC_01 | 8-1 | 01 | 5w | 1:I:1:08 | 1756-IV16 | QD_SUM
|  | 30V |  |  |  | 10 | sw |  |  |  | TB-18 | 26 |  |  | TS_PLC_01
|  | GND |  |  |  | 11 | br |  |  |  | TB-18 | 27 | sw |  | TS_PLC_01
|  | QUENCNO |  |  |  | 12 | sw |  |  |  | TB-18 | 28 |  |  | TS_PLC_01
|  | QUENCM |  |  |  | 13 | or |  |  |  | TB-18 | 29 |  |  | TS_PLC_01
|  | QUENCNC |  |  |  | 14 | sw |  |  |  | TB-18 | 30 |  |  | TS_PLC_01
Reset Inputs
Connector P6 | Normaly 30V at this pin | RESET |  |  |  | 1 | ws |  |  |  | TB-18 | 31 | ws |  | TS_PLC_04 | 15-1 | 04 | w,bk | 1:O:4/15 | 1756-OW16I | Danf Quench Reset
|  | RRTN |  |  |  | 2 | rt |  |  |  | TB-18 | 32 | rt |  | TS_PLC_04 | 15-2 | 04 | w,r | 104350 | 1756-OW16I | Danf Quench Reset
Power Supply
Course Current Transducer signal | 0-3 V |  | V+ |  | MPS-cable1 | 3 | rt | TS-23 | 15 | sw | SCM5B31-03D | 3 | 11 | bl | TS_PLC_07 | 15-1 | 07 | TP-16 ws | 1:I:7:CH 13 + | 1756-IF16 | PSU_Ic
|  |  | V - |  | MPS-cable1 | 4 | sw | TS-23 | 16 | rt | Voltage Input | 2 | 12 | sw |  | 15-2 | 07 | TP-16 sw | 1:I:7:CH 13 -
+/- 10 VDC
4-4 #
Interlock |  | MPS_Fast_Discharge |  | LiYCY 4 * .14 | MPS_DIS | 5 | ws
|  | MPS_Fast_Discharge |  | LiYCY 4 * .14 | MPS_DIS | 6 | br
|  | MPS_Slow_Discharge |  | LiYCY 4 * .14 | MPS_DIS | 3 | gn
Spare SLOW |  | MPS_Slow_Discharge |  | LiYCY 4 * .14 | MPS_DIS | 4 | ge
PLC_E/S_Relay | [18 empty] | Dipole:4:O.Ch12Data | 1756-OW16I | 1756-OW16I
PLC_Slow_relay | [18 empty] | Dipole:4:O.Ch11Data | 1756-OW16I | 1756-OW16I
NMR
Power On/OFF Relay | 24V to pwr Relay
Keep Alive
PLC_KeepAlive_relay | [18 empty] | Dipole:4:O.Ch9Data | 1756-OW16I | 1756-OW16I
Status
Note on C56: Temperature sensor on the current leads. Warm temperatures.
Note on C61: Temperature sensor on the current leads. Warm temperatures.
Note on C193: JT Control Valve for liquid helium supply to the magnet during cool down
Note on C194: JT Control Valve for liquid helium supply to the magnet during cool down
Note on C195: JT Control Valve for liquid helium supply to the magnet during cool down
Note on C196: JT Control Valve for liquid helium supply to the magnet during cool down
Note on C304: Sensors on the right strain stud at corner #1 of HMS dipole
Note on C317: sensors on the left strain stud at corner #1 of HMS dipole
Note on C411: Voltage tap on the warm end of the current lead which is connected with the pancake#1 of the left coil
Note on C412: Voltage tap on the cold end of the current lead which is connected with the opancake #1 of the left coil
Note on C413: Voltage tap at the end of the beginning of the left coil pancake #2
Note on C414: Voltage tap at the end of the left coil pancake
Note on C415: Voltage tap at the begin of the left coil pancake.
Note on C416: : Voltage tap at the end of the left coil pancake #2
Note on C417: Voltage tap at the begin of the left coil pancake #3
Note on C418: Voltage tap at the end of the left coil pancake#3
Note on C419: Voltage tap at the begin of the right coil pancake #4
Note on C420: Voltage tap at the end of the right coil pancake #4
Note on C421: Voltage tap at the begin of the right coil pancake#5
Note on C422: Voltage tap at the end of the right coil pancake#5
Note on C423: Voltage tap at the begin of the right coil pancake#6
Note on C424: Voltage tap at the end of the right coil pancake#6
Note on C425: Voltage tap on the cold end of the current lead which is connected with the pancake #6 of the left coil
Note on C426: Voltage tap on the warm end of the current lead which is connected with the pancake #6 of the left coil
Note on F48: Reservoir-Top-Plate:Located -Temperature of the output pipe
Note on F113: Reservoir-Top-plate: Tem perature of the current Lead Cold End

## PLC I-0 Table
PLC I/O Usage Table
Module | IB16D | OW16I | OW16I | OW16I | IF16 | IF16 | IF16 | IF16 | IF16
Configuration |  |  |  |  | Single_Ended voltage | Single_Ended Current | Single_Ended Voltage/Current | Single_Ended Voltage | Differential_Mode Voltage
Chasis Slot # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Channel
0 | Danf_QD_U1 | MOT_JTV12_Close | MOT_JTV1_Open | MOT_JTV9_Open | T_He_LCLW | m_flow_LCL | T_HX_He |  | VT_1_a to VT_2_a
1 | Danf_QD_L1 | MOT_JTV12_Open | MOT_JTV1_Close | MOT_JTV9_Close | T_He_RCLW | m_flow_RCL | LVDT_JTV1 |  | VT_3_a to VT_4_a
2 | Danf_QD_U2 |  | MOT_JTV2_Open | MOT_JTV10_Open | T_LN2_1 | Warm_Return_Position | LVDT_JTV2 |  | VT_5_a to VT_6_a
3 | Danf_QD_L2 |  | MOT_JTV2_Close | MOT_JTV10_Close | T_LN2_2 |  | LVDT_JTV3 |  | VT_7_a to VT_8_a
4 | Danf_QD_U3 |  | MOT_JTV3_Open | Warm_return_Open | T_LN2_3 | h_LN2 | LVDT_JTV4 |  | VT_9_a to VT_10_a
5 | Danf_QD_L3 |  | MOT_JTV3_Close | Warm_return_Close | T_LN2_4 |  | LVDT_JTV5 |  | VT_11_a to VT_12_a
6 | Danf_QD_U4 |  | MOT_JTV4_Open | h_Lhe_Current_enabled | T_LN2_IN |  | LVDT_JTV6 |  | VT_13_a to VT_14_a
7 | Danf_QD_L4 |  | MOT_JTV4_Close | Penning HV | T_LN2_OUT |  | LVDT_JTV7 |  | VT_15_a to VT_16_a
8 | Danf_QD_Sum |  | MOT_JTV5_Open | Keep_Alive_Reset | T_LHe_1 |  | LVDT_JTV8 | F_R1 | N/A
9 |  |  | MOT_JTV5_Close | Keep_Alive_Control | T_LHe_2 |  | LVDT_JTV9 | F_L1 | N/A
10 |  |  | MOT_JTV6_Open | NMR_Pwr | T_LHe_3 | p_He | LVDT_JTV10 | F_R2 | N/A
11 | JVT Mtrs KS remote |  | MOT_JTV6-Close | PLC_Fast_Relay | T_LHe_4 | p_N2 | T_HX_N2 | F_L2 | N/A
12 | PSU_Control_pwr_on |  | MOT_JTV7_Open | PLC_Slow_Relay | T_LHe_IN | Themo_Vac | LVDT_JTV12 | F_R3 | N/A
13 | PSU_Main_pwr_on |  | MOT_JTV7_Close | PSU_CPU_Reset | T_LHe_OUT | Penning_Vac | MPS_Current_Signal | F_L3 | N/A
14 | PSU_ready |  | MOT_JTV8_Open | PSU_diodes_Reset | T_LHe_LCLC | T_transfer_N2 |  | F_R4 | N/A
15 | PSU_Sum_Interlocks |  | MOT_JTV8_Close | Danf_QD_Reset | T_LHe_RCLC | h_LHe |  | F_L4 | N/A
Datafroth Signal Conditioner Table SCM5B modules
Rack | 1 | 2 | 3 | 4 | 5 | 6
Channel
1 | 34-1562 [RTD - +/- 5V] | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
2 | 34-1562 [RTD - +/- 5V] | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
3 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
4 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
5 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
6 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
7 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
8 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]

## Sheet1
| CGR-1-500 | 120uA |  | 5B03 | 1756-IF16 | Resolution
temp | R | milliV | delta | V | V | 8e-05
4 | 669.06 | 80.2872 | #VALUE! | 4.0144
4.2 | 584.6 | 70.152 | -10.1352 | 3.5076
4.4 | 63.822 | 7.6586 | -62.4934 | 0.38293
4.6 | 63.468 | 7.6162 | -0.04248 | 0.38081
4.8 | 63.114 | 7.5737 | -0.04248 | 0.37868
6 | 60.99 | 7.3188 | -0.25488 | 0.36594
8 | 57.45 | 6.894 | -0.4248 | 0.3447
10 | 53.91 | 6.4692 | -0.4248 | 0.32346
20 | 36.21 | 4.3452 | -2.124 | 0.21726
40 | 22.211 | 2.6653 | -1.6799 | 0.13327
60 | 17.951 | 2.1541 | -0.5112 | 0.10771
77 | 14.33 | 1.7196 | -0.43452 | 0.08598
100 | 10.477 | 1.2572 | -0.46236 | 0.062862
140 | 10.101 | 1.2121 | -0.04512 | 0.060606
180 | 9.725 | 1.167 | -0.04512 | 0.05835
220 | 9.349 | 1.1219 | -0.04512 | 0.056094
260 | 8.973 | 1.0768 | -0.04512 | 0.053838
270 | 8.879 | 1.0655 | -0.01128 | 0.053274
280 | 8.785 | 1.0542 | -0.01128 | 0.05271
282 | 8.7662 | 1.0519 | -0.002256 | 0.052597
284 | 8.7474 | 1.0497 | -0.002256 | 0.052484
286 | 8.7286 | 1.0474 | -0.002256 | 0.052372
288 | 8.7098 | 1.0452 | -0.002256 | 0.052259
290 | 8.691 | 1.0429 | -0.002256 | 0.052146
292 | 8.6722 | 1.0407 | -0.002256 | 0.052033
294 | 8.6534 | 1.0384 | -0.002256 | 0.05192
296 | 8.6346 | 1.0362 | -0.002256 | 0.051808
298 | 8.6158 | 1.0339 | -0.002256 | 0.051695
300 | 8.597 | 1.0316 | -0.002256 | 0.051582
305 | 8.55 | 1.026 | -0.00564 | 0.0513