## PLC Modules Software
|  |  | Date 1/14/2010 | Allen Bradley Hardware | Discounted | Total
Qty | In Use | Spare | Catalog # | Description | Unit Price | Cost | PLC Chassis | Dipole/Cryo | Q3 | Q2 | Q1 | Rotation | PSU-ascii
Software
1 |  |  | 9324-RLD700NXENE | RS-Logix 5000 Pro Edition | 5500 | 5500
1 |  |  | 9701-VWSTENE | RSVIEW Studio | 1995 | 1995
1 |  |  | 9701-VWSS100LENE | RSView Enterprise 100 displays | 4620 | 4620
1 |  |  | 9701-VWSS025LENE | RSView Enterprise 25 displays | 3100 | 3100
3 |  | 1 | 9701-VWSCWAENE | SE Client | 2200 | 6600
1 |  |  | OPC-ABSTE-NA00 | OPC server suite | 795 | 795
1 |  |  | 9301-OPCSRVENE | KPServer | 2000 | 2000
1 |  |  | 9356-PRO2100 | RSSQL Prof 150 Tags | 2800 | 2800
1 |  |  | 9357-CNETMDAD3E | LICENSE KEY FOR CONTROL NET DIAGNOSTIC | 795 | 795
1 |  |  |  | PC server | 2720 | 2720
HARDWARE / PLC
1 | 0 | 1 | 1756-A4 | 4 SLOT CONTROLLOGIX CHASSIS | 191.62 | 191.62
2 | 2 | 0 | 1756-A7 | 7 SLOT CONTROLLOGIX CHASSIS | 291.55 | 583.1 | 2
8 | 5 | 3 | 1756-A10 | 10 SLOT CONTROLLOGIX CHASSIS | 357.97 | 2863.76 |  | 1 | 1 | 1 | 1 | 1
3 | 2 | 1 | 1756-L55 | LOGIX5555 PROCESSOR WITH 1.5 MBYTE NV MEMORY | 3482.33 | 10446.99 | 2
3 | 2 | 1 | 1756-L55M23 | 3.5 MBYTE NV MEMORY | 3287.76 | 9863.28 | 2
2 | 2 | 0 | 1757-SRM | SYSTEM REDUNDANCY MODULE | 3110.25 | 6220.5 | 2
13 | 7 | 6 | 1756-CNB | CONTROLNET BRIDGE MODULE | 867.25 | 11274.25 | 2 | 1 | 1 | 1 | 1 | 1
3 | 2 | 1 | 1756-ENBT | CLX ETHERNET/IP 10/100 BRIDGE MODULE - TWISTED PR | 1098.36 | 3295.08 | 2
12 | 5 | 6 | 1756-N2 | EMPTY SLOT FILLER CARD (ONE FILLER PER PACKAGE) | 13.29 | 159.48 | 4 |  |  |  |  | 1
4 | 3 | 1 | 1786-XT | CONTROLNET 75 OHM TERMINATOR PLUG | 4.66 | 18.64 | 2 | [5 empty] | 1
16 | 8 | 8 | 1786-TPS | CONTROLNET T-TAP/STRAIGHT | 70.71 | 1131.36 | 2 | 1 | 1 | 1 | 1 | 1 | 1
1 | 1 | 0 | 1786-RG6 | CONTROLNET RG6 SHIELD HIGH FLEX CABLE-1000FT ROLL | 407.93 | 407.93 | 1
2 | 2 | 0 | 1757-SRC1 | 1757 REDUNDANCY MODULE CABLE - 1 METER, 3.28FT | 103.33 | 206.66 | 2
12 | 7 | 5 | 1756-PA72 | 85-265 VAC POWER SUPPLY (5V @ 10 AMP) | 531.42 | 6377.04 | 2 | 1 | 1 | 1 | 1 | 1
4 | 1 | 3 | 1794-PS13 | 85-264 VAC TO 24 VDC 1.3A POWER SUPPLY | 121.61 | 486.44 | [6 empty] | 1
6 | 3 | 3 | 1756-BA1 | BATTERY |  |  | 2
I/O Modules
2 | 1 | 1 | 1756-HSC | 2 CHANNEL / 4 OUTPUT HIGH SPEED COUNTER (36 PIN) | 681.73 | 1363.46 | [5 empty] | 1
1 | 0 | 1 | 1756-IA16 | 79-132 VAC INPUT 16 PTS (20 PIN) | 269.01 | 269.01
10 | 6 | 4 | 1756-IB16D | 10-30 VDC DIAGNOSTIC INPUT 16 PTS (36 PIN) | 357.97 | 3579.7 |  |  | 1 | 1 | 1 | 3
20 | 17 | 3 | 1756-IF16 | ANALOG INPUT - CURRENT/VOLTAGE 16 PTS (36 PIN) | 921.25 | 18425 |  | 5 | 4 | 4 | 4
7 | 4 | 3 | 1756-IV16 | 79-132 VAC INPUT 16 PTS (20 PIN) | 408 | 2856 |  | 1 | 1 | 1 | 1
9 | 2 | 7 | 1756-OB16D | 19-30 VDC DIAGNOSTIC OUTPUT 16 PTS (36 PIN) | 479.05 | 4311.45 | [5 empty] | 2
3 | 0 | 3 | 1756-OF6CI | ISOLATED ANALOG OUTPUT - CURRENT 6 PTS (20 PIN) | 1485.06 | 4455.18
4 | 4 | 0 | 1756-OF6VI | ISOLATED ANALOG OUTPUT - VOLTAGE 6 pts (20 PIN) | 1485.06 | 5940.24 |  |  | 1 | 1 | 1 | 1
13 | 10 | 3 | 1756-OW16I | N.O. ISOLATED RELAY OUTPUT 16 PTS (36 PIN) | 369.04 | 4797.52 |  | 3 | 2 | 2 | 2 | 1
4 | 1 | 3 | 1794-ACN15 | SINGLE MEDIA ADAPTER FOR CONTROLNET | 442.2 | 1768.8 | [6 empty] | 1
8 | 5 | 3 | MVI94-GSC | Prosoft ASCII Generic Serial Communication Module | 1056 | 8448 |  | 1 |  |  |  |  | 4
MISC
56 | 39 | 17 | 1756-TBCH | 36 PIN SCREW CLAMP BLOCK WITH STANDARD HOUSING | 44.28 | 2479.68 |  | 8 | 8 | 8 | 8 | 7
11 | 8 | 3 | 1756-TBNH | 20 POSITION NEMA SCREW CLAMP BLOCK | 33.17 | 364.87 |  | 1 | 2 | 2 | 2 | 1 | 0
1 | 1 | 1 | 1784-PCICS | CONTROLNET PCI BUS SCANNER CARD | 1091.69 | 1091.69 |  | 1
5 | 4 | 1 | 800T-H33B | SWITCH SELECTOR Keyed 2 POSITION | 128.45 | 642.25 |  | 1 | 1 | 1 | 1
44 | 41 | 3 | 800T-J91A | SWITCH SELECTOR 3 POSITION | 71.24 | 3134.56 |  | 11 | 10 | 10 | 10
61 | 61 | 0 | G020 | BREAKERS 2amps | 54.3 | 3312.3 |  | 13 | 16 | 16 | 16
1 | 1 | 0 | G050 | BREAKERS 5amps | 54.3 | 54.3 |  | 1
3 | 2 | 1 | G080 | BREAKERS 8amps | 54.3 | 162.9 |  | 2
6 | 6 | 0 | G100 | BREAKERS 10amps | 54.3 | 325.8 |  |  | 2 | 2 | 2
[5 empty] | Subtotal: | 148378.54

## Signal Conditioners
|  |  |  | Date Jan. 14, 2010 | DataForth Signal Conditioners + LVDT
Qty | Spare | Failed | Used | Catalog # | Description | Price | Ext. Price
Magnets
49 | 2 | 1 | 46 | SCM5B-34-1562 | RTD custom | 240 | 11760
23 | 6 |  | 20 | SCM5B-30-02D | Analog Input Narrow bandwidth 50mV in / 10V out | 150 | 3450
3 | 6 |  | 20 | SCM5B-30-07D | Analog Input Narrow bandwidth 1V in / 10V out | 150 | 450
21 | 5 |  | 16 | SCM5B-31-03D | Analog Voltage Input Module 10V in / 5V out | 150 | 3150
36 | 3 |  | 33 | SCM5B-31-09D | Analog Voltage Input Module 40V in / 5V out | 150 | 5400
22 | 6 |  | 16 | SCM5B-38-35D | Strain Gage Input Module | 180 | 3960
0 | 1 |  |  | SCM5B-38-36D | Strain Gage Input Module | 180 | 0
10 | 1 |  | 9 | SCM5B-43-05D | General Purpose with excitation 5V in / 10V out | 205 | 2050
21 | 0 |  | 21 | SCMXCA-004 12 | Cable | 50 | 1050
21 | 0 |  | 21 | SCMPB-05-02 | Backplane-8 channels with DIN mounts | 215 | 4515
21 | 0 |  | 21 | SCMXIF-DIN | Breakout Board Din Mounted | 61 | 1281
21 | 0 |  | 21 | SCMXRK-002 | Rack Mounting Plate 19" | 39 | 819
46 | 5 | 4 | 37 | LVC-2402 / 2412 | LVDT signal conditioner 24Vdc | 320 | 14720
5 | 1 |  | 4 | SDP5-5-100T | PSU 5 volts | 100 | 500
5 | 0 | 1 | 5 | SDP10-24-100P | PSU 24V Psu | 340 | 1700
[6 empty] | 2530 | 54805

## Rack Termination cabling
Date 2/07/2007
I/O Rack / Hardware / Cable
Qty | Catalog # | Description | Price | Disc. Price | Ext. Price
1
|  | Rack Chassis |  | 0.737
1 | XFR-317824 | Vertical Frame 31.562 deep 82.375 Tall 27.562 wide | 663.52 | 663.52 | 663.52
4 | XMA-78 | Mounting Angle Pair | 45 | 45 | 180
1 | XPN-7324 | Panel 73.5" Tall 24" wide | 105 | 105 | 105
1 | DS-XSR-7824 | Front Door | 160 | 160 | 160
1 | DS-XSL-7824 | Rear Door | 160 | 160 | 160
1 | XES-2024 | Equipment Shelf | 36 | 36 | 36
2 | XSP-3178-S | Side Panel | 130 | 130 | 260
1 | XPN-2819 | Top Panel | 40 | 40 | 40
2 | XPN-0324-CAP | Data Cable Access Panel | 28 | 28 | 56
100 | HW-092 | Threaded captive clip nut | 0.4 | 0.4 | 40
100 | HW-103 | #10-32 thread truss head machin screw | 0.28 | 0.28 | 28
1 | 446149 | Latch/Slotted | 4 | 4 | 4
1 | A423008LP | SINGLE DOOR ENCLOSURE HOFFMAN | 750 | 750 | 750
1 | a42p30 | PANEL FOR ENCLOSURE | 175 | 175 | 175
3 | ABA-05 | Panel reducers | 51 | 51 | 153
|  |  | Subtotal: |  | 2810.52
Rack hardware
800 | 1492-W4 | Terminal Blocks Single Level | 1.55 | 1.55 | 1240
100 | 1492-WD3 | Terminal Blocks Double Level | 3.4 | 3.4 | 340
200 | 1492-WTF3 | Terminal Blocks Triple Level | 5.05 | 5.05 | 1010
20 | 1492-EB3 | End barrier for W4 | 0.6 | 0.6 | 12
30 | 1492-EA35 | End Anchor for W4 | 0.9 | 0.9 | 27
30 | 1492-GM35 | Terminal Group marker | 1.85 | 1.85 | 55.5
20 | 1492-EBD3 | End Barrier for WD3 | 1.01 | 1.01 | 20.2
30 | 1492-EAH35 | End Anchor for WD3 | 3.4 | 3.4 | 102
20 | 1492-EBFT3 | End Barrier for WTF3 | 1 | 1 | 20
15 | 1492-SJT5-20-B | JUMPERS 20-POLE PACAKGE OF 10 | 5.5 | 5.5 | 82.5
1 | 800T-H33B | KEYED SELECTOR SWITCH 2-POLE 2NO / 2NC | 133 | 133 | 133
11 | 800T-J91A | SWITCH 3-POSITION STC, 2NO, 2NC | 62 | 62 | 682
1 | 700-ha33z24 | CONTROL RELAY 2PDT 24VDC 8-PIN | 13 | 13 | 13
1 | 700-HN126 | SOCKET FOR CONTROL RELAY | 7 | 7 | 7
2 | 1492-CB1G100 | CIRCUIT BREAKER 10 AMPS | 44 | 44 | 88
10 | 1492-CB1G050 | CIRCUIT BREAKER 5 AMPS | 44 | 44 | 440
10 | 1492-CB1G020 | CIRCUIT BREAKER 2 AMPS | 44 | 44 | 440
10 | 199-DR1 | DIN MOUNTING RAIL | 6.3 | 6.3 | 63
10 | 885-2269 | BANANA JACK DOUBLE, BLACK | 2.4 | 2.4 | 24
1 | 90F7644 | RELAY TIMER | 84 | 84 | 84
|  |  | Subtotal: |  | 4883.2
Cable hardware
30 | D2x4LKG6 | Wire Duct 2" x4" x 6ft length | 8 | 8 | 240
30 | C2LG6 | 2"x 4" Wire Duct cover 6ft length | 2 | 2 | 60
30 | D1.5x4LG6 | Wirer Duct 1.5'x4'x6ft length | 7.5 | 7.5 | 225
30 | C1.5LG6 | 1.5"x4" wire Duct cover 6ft length | 1.5 | 1.5 | 45
20 | 534-1301 | TERMINATION SUPPLIES, FERRULES, ETC | 50 | 50 | 1000
|  |  | Subtotal: |  | 1570
Cables
1 | ALPHA 1736C/R1000 | CABLE 2 COND 22AWG 500 ft | 200 | 200 | 200
7 | ALPHA 5470/25C | CABLE 25 COND 20AWG 500 ft | 4560 | 4560 | 31920
2 | ALPHA 45470/20C | CABLE 20COND 20 AWG 500 ft | 3125 | 3125 | 6250
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  |  | 0 | 0
|  |  | Subtotal: |  | 38370
|  |  |  | Total | 47633.72
Note on A57: FEET
Note on D32: :
Note on D42: POMONA 2269-0
Note on D43: CNT-35-96 TYCO ELECTRONICS
Note on D52: 22AWG FERRULES

## Instrumentation
Instrumentation per Magnet
qty | Spare | part # | description | unit cost | Total Cost
24 |  | PT102-Al SMOD-4-QL32-15 | PT-102 | 300 | 7200
8 |  | CX-1030-CU SMOD-4-QL36-15 | Cerenox 4.2K | 965 | 7720
2 |  | Honeywell FPG1BR,2P5B6A | Pressure 0.4-5 Bar Ln2 & He | 565 | 1130
1 |  | Edwards APG-M-NW16 | 760 to 1x10-3 Torr | 230 | 230
1 |  | Edwards AIM-S-NW16 | 1x10-2 to 1x10-9 Torr | 560 | 560
8 |  | Copper Nickel Alloy Film 120 Ohm GF=2.1 Half Bridge | estimate | 900 | 7200
1 |  | Model 135 Monitor & Probe 80" | L He Meter / probe | 3356 | 3356
1 |  | Model 185 Ln2 level sensor and monitor | L N2 Meter / probe | 2461 | 2461
2 |  | MKS 1559A | Gas He Controller 0-30L/min | 3250 | 6500
36357
1 |  | 3RTP100-2-2 Three axis Hall probe + accessories | Quads / Bender | 3685 | 3685
1 |  | PT2025 + 2040 + 2030 + cable + 4 probes | NMR Assembly (dipole) | 47500 | 47500
6 | 1 | relay board 24 Volts | RB-24
10 | 5 | Constant Current Source Boards
8 | 4 | Quench detector Boards | Danfysk
Note on E4: Lakeshore PT102-Al SMOD-4-QL32-15 $300 Quote #2812 3/6/07
Note on E5: Lakeshore: CX-1030-CU SMOD:4-QL36-15 Calibrated with report Carbon Glass discontiuned Add $165 for SMOD
Note on E6: Honeywell Web page http://www.sensotec.com/pressure_transducer_instock.shtml 3/7/07
Note on E7: From PR 191738 8/23/2000
Note on E8: From PR 191738 8/23/2000
Note on E10: American Magnetics Model 135 Monitor and sensor probe
Note on E11: American Magnetics
Note on E12: Flow Controllers PR# 255827 Model #1559A Calibrated to He gas 4-20mA output
Note on E17: GMW web page Pricing www.GMW.com
Note on E20: GMW web page Pricing www.GMW.com

## Sheet1
Signal description | Range | Qty | Red Qty | Description |  | Magnet Interface Connector | Cable: Magnet to Rack | Signal Conditioner | I/O Signals to PLC | PLC I/O Module
|  |  |  | Internal sensors | Internal Cable
Temperature |  |  |  | Temperature sensors
Temperature Sensor N2 | > 60 K | 6 | 6 | PT100 3-wire LN2 | 12xBelden 9491 (One Triad) | B (50way) | Belden 1084A(8 triads) |  |  | 1756 - IR6I
Temperature Sensor CL | > 233K | 2 | 0 | PT100 3-wire Current Lead Top end | 2xBelden 9491 (One Triad) | C (15pin) | Belden 1084A(8 triads) |  |  | 1756 - IR6I
Temperature Sensor Heat Exchanger | > 60 K | 4 | 4 | PT100 3-wire Cool Down, Return, Cold massx2 | 8xBelden 9491 (One Triad) |  | Belden 1084A(8 triads) |  |  | 1756 - IR6I
Temperature Sensor Cuurent lead | < 60 K | 2 | 2 | CG 3-wire Current Lead Top bottom | 4xBelden 9491 (One Triad) | A (50way) | Belden 1084A(8 triads) | Dataforth SCM5B34 - 1562 RTD Input | +/- 5 VDC | 1756 - IF16
Temperature Sensor He | < 60 K | 4 | 4 | CG 3-wire Coils | 2xBelden 9491 (One Triad) | C (15pin) | Belden 1084A(8 triads) | Dataforth SCM5B34 - 1562 RTD Input | +/- 5 VDC | 1756 - IF16
Temperature Sensor External | 300-4K | 3 | 2 | Diodes 2-wire Cooldown,Supply,Warm Return | 14xBelden 9491 (One Triad) | A (50way) | Belden 1084A(8 triads) | Dataforth SCM5B34 - 1562 RTD Input | +/- 5 VDC | 1756 - IF16
|  | 24 | 14 |  | 38 | Total #pins (A&B) = 96.0 | 5 | 24 (3 boards of 8 conditioners) |  | 2 X16 input modules single ended
Voltage Taps
All Magnets |  | 4 | 2 | Curent Leads | AWG-24 wire HABIA cable AB | D (15pin) |  | SCM-5B31-09D | +/- 10 VDC | 1756 - IF16
Quads |  | 4 | 4 | Coil to Coil Splices | AWG-24 wire HABIA cable AB | D (15pin) |  | SCM-5B31-09D | +/- 10 VDC | 1756 - IF16
Dipoles |  | 2 | 2 | Coil to Coil Splices | AWG-24 wire HABIA cable AB |  |  | SCM-5B31-09D | +/- 10 VDC | 1756 - IF16
Q2/Q3 |  | 12 | 0 | Pancake Splices | AWG-24 wire HABIA cable AB |  |  | SCM-5B31-09D | +/- 10 VDC | 1756 - IF16
Dipoles |  | 6 | 0 | Pancake Splices | AWG-24 wire HABIA cable AB |  |  | SCM-5B31-09D | +/- 10 VDC | 1756 - IF16
External sensors
Pressure |  |  |  | Pressure gauges
LN2 Pressure | 0.4 - 5 Bar | 1 | 0 | P6P/5bar Hottinger Baldwin Gmbh 5V/225Hz strain gauge full bridge | P 3-1 |  |  | Dataforth SCM5B38 - 35D | +/- 10 VDC | 1756 - IF16
LHe Pressure | 0.4 - 5 Bar | 1 | 0 | P6P/5bar Hottinger Baldwin Gmbh 5V/225Hz strain gauge full bridge | P 3-1 |  |  | Dataforth SCM5B38 - 35D | +/- 10 VDC | 1756 - IF16
Vacuum |  |  |  | Vacuum gauges
LH Thermovac TR206 | Vacuum gauge | 1 | 0 | 760 Torr to 1x10-3 Torr | P 3-3 |  |  | Leybold Combivac CM 31 | 0 - 10 VDC | 1756 - IF16
LH PenningVac PR 35 | Vacuum gauge | 1 | 0 | 1x10-2 Torr to 1x10-9 Torr | P 3-3 |  |  | Leybold Combivac CM 31 | 0 - 10 VDC | 1756 - IF16
Strain Gauges |  |  |  | Strain Guages
Gauge | 0 kN to 35 kN | 8 | 8 | CEA-06-125UT-350 Micro-measurement | P 4-1 |  |  | Dataforth SCM5B38 - 35D | +/- 10 VDC | 1756 - IF16
Liquid Level |  |  |  | Level Probes
LN2 Level | 0 - 100 % | 1 | 0 | Capitance 3 wire | P 6-1 |  |  | None | 4-20 mA
LHe Level | 0 - 100 % | 1 | 0 | Superconducting probe 4-wire | P 6-3 |  |  | Dataforth SCM5B31 - 03D | +/- 10 VDC | 1756 - IF16
Gas Flow Meters |  |  |  | Flow Meters
Lead He Gas Flow | 0-2000 sccm N2 | 2 |  | MKS 1749A-02000SV | P 7-1 |  |  | None | 4-20 mA | 1756 - IF16
JT Valves
JT Valve Manual/Auto Switch |  | 1 |  | Switch for all 11 JT valves | [5 empty] | 1756 - IB16D
Jt Valve Motors |  | 10 |  | Globe Motor (24 VDC @ 0.8A) | P 8-2 |  |  | Dataforth DSCA43-15C | 24V dc out to motor. | 1756 - OW16
LVDT | -6-100% | 10 |  | LVDT | P 8-1 |  |  | Macro Sensors LVC-2402 | 4-20 mA | 1756 - IF16
Magnet
Voltage Readings
Main Coil Voltages | +/- 500 VDC | 16 | 16 | AWG-28 wire HABIA cable AB | P 5-1 |  |  | Dataforth SCM5B31-090 | +/- 10 VDC | 1756 - IF16
NMR Unit |  |  |  | NMR
PLC commuications | Ascii | 1 |  | Metrolab Field Regulation RG2040 | P 9-1 |  |  | Flex I/O | RS232 | Control Net
Power on/off relay |  | 1 | [5 empty] | None |  | 1756 - OW16
Power Supply |  |  |  | PSU
PSU Interlocks and Status Signals |  | 16 |  | Interlock and Status Signals from PSU |  |  |  | None | Digital Signal | 1756 - IB16D
PSU Interlocks |  | 2 |  | Interlock Signals to the PSU from PLC |  |  |  | None |  | 1756 - OW16
PSU Reset Signal |  | 1 |  | Reset Signal to PSU & Diodes |  |  |  | None |  | 1756 - OW16
PSU Course Current Signal |  | 1 |  | 3 V dc +/- Dac output from PSU |  |  |  | Dataforth SCM5B31 - 03D | +/- 10 VDC | 1756 - IF16
Quench Detectors
Danfysik 4 Channel |  | 9 |  | Interlock Signals |  |  |  | None | Digital Signal | 1756 - IB16D
|  | 1 |  | Relay Contact |  |  |  | None
|  | 1 |  | Reset Signal |  |  |  | None |  | 1756 - OW16

## Chassis Layout
PLC I/O Usage Table
Module | IB16D | OBD4 | OW16I | OW16I | IF16 | IF16 | IF16 | IF16 | IF16
Configuration |  |  |  |  | Single_Ended voltage | Single_Ended Current | Single_Ended Voltage/Current | Single_Ended Voltage | Differential_Mode Voltage
Chasis Slot # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
Channel
0 | Danf_QD_U1 | CL mass flow + | MOT_JTV1_Open | MOT_JTV9_Open | T_He_LCLW | m_flow_LCL | T_HX_He |  | VT_1_a to VT_2_a
1 | Danf_QD_L1 | CL mass f flow - | MOT_JTV1_Close | MOT_JTV9_Close | T_He_RCLW | m_flow_RCL | LVDT_JTV1 |  | VT_3_a to VT_4_a
2 | Danf_QD_U2 |  | MOT_JTV2_Open | MOT_JTV10_Open | T_LN2_1 | Warm_Return_Position | LVDT_JTV2 |  | VT_5_a to VT_6_a
3 | Danf_QD_L2 |  | MOT_JTV2_Close | MOT_JTV10_Close | T_LN2_2 |  | LVDT_JTV3 |  | VT_7_a to VT_8_a
4 | Danf_QD_U3 |  | MOT_JTV3_Open | Warm_return_Open | T_LN2_3 | h_LN2 | LVDT_JTV4 |  | VT_9_a to VT_10_a
5 | Danf_QD_L3 |  | MOT_JTV3_Close | Warm_return_Close | T_LN2_4 |  | LVDT_JTV5 |  | VT_11_a to VT_12_a
6 | Danf_QD_U4 |  | MOT_JTV4_Open | h_Lhe_Current_enabled | T_LN2_IN |  | LVDT_JTV6 |  | VT_13_a to VT_14_a
7 | Danf_QD_L4 |  | MOT_JTV4_Close | Penning HV | T_LN2_OUT |  | LVDT_JTV7 |  | VT_15_a to VT_16_a
8 | Danf_QD_Sum |  | MOT_JTV5_Open | Keep_Alive_Reset | T_LHe_1 |  | LVDT_JTV8 | F_R1 | N/A
9 |  |  | MOT_JTV5_Close | Keep_Alive_Control | T_LHe_2 |  | LVDT_JTV9 | F_L1 | N/A
10 |  |  | MOT_JTV6_Open | NMR_Pwr | T_LHe_3 | p_He | LVDT_JTV10 | F_R2 | N/A
11 | JVT Mtrs KS remote |  | MOT_JTV6-Close | PLC_Fast_Relay | T_LHe_4 | p_N2 | T_HX_N2 | F_L2 | N/A
12 | PSU_Control_pwr_on |  | MOT_JTV7_Open | PLC_Slow_Relay | T_LHe_IN | Themo_Vac | LVDT_JTV12 | F_R3 | N/A
13 | PSU_Main_pwr_on |  | MOT_JTV7_Close | PSU_CPU_Reset | T_LHe_OUT | Penning_Vac | MPS_Current_Signal | F_L3 | N/A
14 | PSU_ready |  | MOT_JTV8_Open | PSU_diodes_Reset | T_LHe_LCLC | T_transfer_N2 |  | F_R4 | N/A
15 | PSU_Sum_Interlocks |  | MOT_JTV8_Close | Danf_QD_Reset | T_LHe_RCLC | h_LHe |  | F_L4 | N/A
Datafroth Signal Conditioner Table SCM5B modules
Rack | 1 | 2 | 3 | 4 | 5 | 6
Channel
1 | 34-1562 [RTD - +/- 5V] | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
2 | 34-1562 [RTD - +/- 5V] | 34-1562 [RTD - +/- 5V] | 30-02D [+/-50mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
3 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
4 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] | 31-03D [+/-10V - +/-10V] | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
5 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
6 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
7 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]
8 | 34-1562 [RTD - +/- 5V] |  | 30-02D [+/-50mV - +/-10V] |  | 38-35D [+/-20mV - +/-10V] | 31-09D [+/-40mV - +/-10V]