## Summary
Signal description | Range | Qty | Red Qty | Description
Internal sensors
Temperature |  |  |  | Temperature sensors
Temperature Sensor N2 | > 60 K | 6 | 6 | PT100 3-wire LN2
Temperature Sensor CL | > 233K | 2 | 0 | PT100 3-wire Current Lead Top end
|  | 4 | 4 | PT100 3-wire Cool Down, Return, Cold massx2
|  | 2 | 2 | CG 3-wire Current Lead Top bottom
Temperature Sensor He | > 60 K | 4 | 4 | CG 3-wire Coils
Temperature Sensor He | > 60 K | 3 | 2 | Diodes 2-wire Cooldown,Supply,Warm Return
|  | 24 | 14
Voltage Taps
|  | 4 | 2 | Curent Leads
|  | 4 | 4 | Coil to Coil Splices (Q1)
|  | 16 | 0 | Pancake Splices
External sensors
Pressure |  |  |  | Pressure gauges
LN2 Pressure | 0.4 - 5 Bar | 1 | 0 | P6P/5bar Hottinger Baldwin Gmbh 5V/225Hz strain gauge full bridge
LHe Pressure | 0.4 - 5 Bar | 1 | 0 | P6P/5bar Hottinger Baldwin Gmbh 5V/225Hz strain gauge full bridge
Vacuum |  |  |  | Vacuum gauges
LH Thermovac TR206 | Vacuum gauge | 1 | 0 | 760 Torr to 1x10-3 Torr
LH PenningVac PR 35 | Vacuum gauge | 1 | 0 | 1x10-2 Torr to 1x10-9 Torr
Strain Gauges |  |  |  | Strain Guages
Gauge | 0 kN to 35 kN | 8 | 8 | CEA-06-125UT-350 Micro-measurement
Liquid Level |  |  |  | Level Probes
LN2 Level | 0 - 100 % | 1 | 0 | Capitance 3 wire
LHe Level | 0 - 100 % | 1 | 0 | Superconducting probe 4-wire
Gas Flow Meters |  |  |  | Flow Meters
Lead He Gas Flow | 0-2000 sccm N2 | 2 |  | MKS 1749A-02000SV
JT Valves
JT Valve Manual/Auto Switch |  | 1 |  | Switch for all 11 JT valves
Jt Valve Motors |  | 10 |  | Globe Motor (24 VDC @ 0.8A)
LVDT | -6-100% | 10 |  | LVDT
Magnet
Voltage Readings
Main Coil Voltages | +/- 500 VDC | 16 | 16 | AWG-28 wire HABIA cable AB
NMR Unit |  |  |  | NMR
PLC commuications | Ascii | 1 |  | Metrolab Field Regulation RG2040
Power on/off relay |  | 1
Power Supply |  |  |  | PSU
PSU Interlocks and Status Signals |  | 16 |  | Interlock and Status Signals from PSU
PSU Interlocks |  | 2 |  | Interlock Signals to the PSU from PLC
PSU Reset Signal |  | 1 |  | Reset Signal to PSU & Diodes
PSU Course Current Signal |  | 1 |  | 3 V dc +/- Dac output from PSU
Quench Detectors
Danfysik 4 Channel |  | 9 |  | Interlock Signals
|  | 1 |  | Relay Contact
|  | 1 |  | Reset Signal

## Signal List
Sensor | Device | Range | Sensor | Signal | Connector | Connector | Cable | Cable | Wire | Term Strip | Pin | Cable | Cable | Wire | Connector | Signal | DataForth | Pin | Cable | Cable | Wire | Term Strip | Pin | Cable | Cable | Wire | I/O Channel | I/O Module | PLC
Count | Temperature |  | Name |  |  | Pin # | Label | Type | Color |  | Row-block | Label | Type | Color | Panel/slot/Pin | Conditioner | SCMXIF-DIN | Out | Label | Type | Color |  | Row-block | Label | Type | Color |  |  | Tag Name
Carbon Glass
1 | T_Coil_1 | 60-4K | CG-1 | V+ | IC-1 | 2 | 235-05 | Belden 9546 |  | CR-TS-10 | 2-1 | 235-01 | Alpha 1896 | WT | DF 1-0-3 | SCM5B30-02D | 1 | 1 | 236-07 | Alpha 6039C | BL | TS-PLC-06 | 0-1 | 306-01 | Belden 22676 | 1/WT | 1:I:6:CH 0 + | 1756-IF16 | T_Coil_1
|  |  | CG-1 | V- | IC-1 | 3 | 235-05 | Belden 9546 |  | CR-TS-10 | 3-1 | 235-01 | Alpha 1896 | GN | DF 1-0-2 | SCM5B30-02D | 1 | 3 | 236-07 | Alpha 6039C | BK | TS-PLC-06 | 0-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  | CG-1 | I+ | IC-1 | 1 | 235-05 | Belden 9546 |  | CR-TS-10 | 1-1 | 235-01 | Alpha 1896 | RD | CCS Board A |  | J1 | CH 1 +
|  |  | CG-1 | I- | IC-1 | 4 | 235-05 | Belden 9546 |  | CR-TS-10 | 4-1 | 235-01 | Alpha 1896 | BK | CCS Board A |  | J1 | CH 1 -
2 | T_Coil_1 | 60-4K | CG-1_R | V+ | IC-2 | 2 | 235-05-R | Belden 9546 |  | CR-TS-10 | 2-2
| Redundant |  | CG-1_R | V- | IC-2 | 3 | 235-05-R | Belden 9546 |  | CR-TS-10 | 3-2
|  |  | CG-1_R | I+ | IC-2 | 1 | 235-05-R | Belden 9546 |  | CR-TS-10 | 1-2
|  |  | CG-1_R | I- | IC-2 | 4 | 235-05-R | Belden 9546 |  | CR-TS-10 | 4-2
3 | T_Coil_2 | 60-4K | CG-2 | V+ | IC-1 | 6 | 235-05 | Belden 9546 |  | CR-TS-10 | 6-1 | 235-02 | Alpha 1896 | WT | DF 1-1-3 | SCM5B30-02D | 1 | 5 | 236-07 | Alpha 6039C | YL | TS-PLC-06 | 1-1 | 306-01 | Belden 22676 | 1/BK | 1:I:6:CH 1 + | 1756-IF16 | T_Coil_2
|  |  | CG-2 | V- | IC-1 | 7 | 235-05 | Belden 9546 |  | CR-TS-10 | 7-1 | 235-02 | Alpha 1896 | GN | DF 1-1-2 | SCM5B30-02D | 1 | 6 | 236-07 | Alpha 6039C | BK | TS-PLC-06 | 1-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  | CG-2 | I+ | IC-1 | 5 | 235-05 | Belden 9546 |  | CR-TS-10 | 5-1 | 235-02 | Alpha 1896 | RD | CCS Board A |  | J1 | CH 2 +
|  |  | CG-2 | I- | IC-1 | 8 | 235-05 | Belden 9546 |  | CR-TS-10 | 8-1 | 235-02 | Alpha 1896 | BK | CCS Board A |  | J1 | CH 2 -
4 | T_Coil_2 | 60-4K | CG-2_R | V+ | IC-2 | 6 | 235-05-R | Belden 9546 |  | CR-TS-10 | 6-2
| Redundant |  | CG-2_R | V- | IC-2 | 7 | 235-05-R | Belden 9546 |  | CR-TS-10 | 7-2
|  |  | CG-2_R | I+ | IC-2 | 5 | 235-05-R | Belden 9546 |  | CR-TS-10 | 5-2
|  |  | CG-2_R | I- | IC-2 | 8 | 235-05-R | Belden 9546 |  | CR-TS-10 | 8-2
5 | T_Coil_3 | 60-4K | CG-3 | V+ | IC-1 | 10 | 235-05 | Belden 9546 |  | CR-TS-10 | 10-1 | 235-03 | Alpha 1896 | WT | DF 1-2-3 | SCM5B30-02D | 1 | 7 | 236-07 | Alpha 6039C | BN | TS-PLC-06 | 2-1 | 306-01 | Belden 22676 | 2/WT | 1:I:6:CH 2 + | 1756-IF16 | T_Coil_3
|  |  | CG-3 | V- | IC-1 | 11 | 235-05 | Belden 9546 |  | CR-TS-10 | 11-1 | 235-03 | Alpha 1896 | GN | DF 1-2-2 | SCM5B30-02D | 1 | 9 | 236-07 | Alpha 6039C | BK | TS-PLC-06 | 2-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  | CG-3 | I+ | IC-1 | 9 | 235-05 | Belden 9546 |  | CR-TS-10 | 9-1 | 235-03 | Alpha 1896 | RD | CCS Board A |  | J1 | CH 3 +
|  |  | CG-3 | I- | IC-1 | 12 | 235-05 | Belden 9546 |  | CR-TS-10 | 12-1 | 235-03 | Alpha 1896 | BK | CCS Board A |  | J1 | CH 3 -
6 | T_Coil_3 | 60-4K | CG-3_R | V+ | IC-2 | 10 | 235-05-R | Belden 9546 |  | CR-TS-10 | 10-2
| Redundant |  | CG-3_R | V- | IC-2 | 11 | 235-05-R | Belden 9546 |  | CR-TS-10 | 11-2
|  |  | CG-3_R | I+ | IC-2 | 9 | 235-05-R | Belden 9546 |  | CR-TS-10 | 9-2
|  |  | CG-3_R | I- | IC-2 | 12 | 235-05-R | Belden 9546 |  | CR-TS-10 | 12-2
7 | T_Coil_4 | 60-4K | CG-4 | V+ | IC-1 | 14 | 235-05 | Belden 9546 |  | CR-TS-10 | 14-1 | 235-04 | Alpha 1896 | WT | DF 1-3-3 | SCM5B30-02D | 1 | 11 | 236-07 | Alpha 6039C | OR | TS-PLC-06 | 3-1 | 306-01 | Belden 22676 | 2/BK | 1:I:6:CH 3 + | 1756-IF16 | T_Coil_4
|  |  | CG-4 | V- | IC-1 | 15 | 235-05 | Belden 9546 |  | CR-TS-10 | 15-1 | 235-04 | Alpha 1896 | GN | DF 1-3-2 | SCM5B30-02D | 1 | 12 | 236-07 | Alpha 6039C | BK | TS-PLC-06 | 3-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  | CG-4 | I+ | IC-1 | 13 | 235-05 | Belden 9546 |  | CR-TS-10 | 13-1 | 235-04 | Alpha 1896 | RD | CCS Board A |  | J1 | CH 4 +
|  |  | CG-4 | I- | IC-1 | 16 | 235-05 | Belden 9546 |  | CR-TS-10 | 16-1 | 235-04 | Alpha 1896 | BK | CCS Board A |  | J1 | CH 4 -
8 | T_Coil_4 | 60-4K | CG-4_R | V+ | IC-2 | 14 | 235-05-R | Belden 9546 |  | CR-TS-10 | 14-2
| Redundant |  | CG-4_R | V- | IC-2 | 15 | 235-05-R | Belden 9546 |  | CR-TS-10 | 15-2
|  |  | CG-4_R | I+ | IC-2 | 13 | 235-05-R | Belden 9546 |  | CR-TS-10 | 13-2
|  |  | CG-4_R | I- | IC-2 | 16 | 235-05-R | Belden 9546 |  | CR-TS-10 | 16-2
9 | T_CL_N_C | 60-4K | CG-5 | V+ | IC-1 | 18 | 235-05 | Belden 9546 |  | CR-TS-10 | 18-1 | 236-01 | Alpha 1896 | WT | DF 1-4-3 | SCM5B30-02D | 1 | 13 | 236-07 | Alpha 6039C | RD | TS-PLC-06 | 5-1 | 306-01 | Belden 22676 | 3/WT | 1:I:6:CH 4 + | 1756-IF16 | T_CL_N_C
|  |  | CG-5 | V- | IC-1 | 19 | 235-05 | Belden 9546 |  | CR-TS-10 | 19-1 | 236-01 | Alpha 1896 | GN | DF 1-4-2 | SCM5B30-02D | 1 | 15 | 236-07 | Alpha 6039C | BK | TS-PLC-06 | 5-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  | CG-5 | I+ | IC-1 | 17 | 235-05 | Belden 9546 |  | CR-TS-10 | 17-1 | 236-01 | Alpha 1896 | RD | CCS Board A |  | J1 | CH 5 +
|  |  | CG-5 | I- | IC-1 | 20 | 235-05 | Belden 9546 |  | CR-TS-10 | 20-1 | 236-01 | Alpha 1896 | BK | CCS Board A |  | J1 | CH 5 -
10 | T_CL_N_C | 60-4K | CG-5_R | V+ | IC-2 | 18 | 235-05-R | Belden 9546 |  | CR-TS-10 | 18-2
| Redundant |  | CG-5_R | V- | IC-2 | 19 | 235-05-R | Belden 9546 |  | CR-TS-10 | 19-2
|  |  | CG-5_R | I+ | IC-2 | 17 | 235-05-R | Belden 9546 |  | CR-TS-10 | 17-2
|  |  | CG-5_R | I- | IC-2 | 20 | 235-05-R | Belden 9546 |  | CR-TS-10 | 20-2
11 | T_CL_P_C | 60-4K | CG-6 | V+ | IC-1 | 22 | 235-05 | Belden 9546 |  | CR-TS-10 | 22-1 | 236-02 | Alpha 1896 | WT | DF 1-5-3 | SCM5B30-02D | 1 | 17 | 236-07 | Alpha 6039C | GN | TS-PLC-06 | 6-1 | 306-01 | Belden 22676 | 3/BK | 1:I:6:CH 5 + | 1756-IF16 | T_CL_P_C
|  |  | CG-6 | V- | IC-1 | 23 | 235-05 | Belden 9546 |  | CR-TS-10 | 23-1 | 236-02 | Alpha 1896 | GN | DF 1-5-2 | SCM5B30-02D | 1 | 18 | 236-07 | Alpha 6039C | BK | TS-PLC-06 | 6-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  | CG-6 | I+ | IC-1 | 21 | 235-05 | Belden 9546 |  | CR-TS-10 | 21-1 | 236-02 | Alpha 1896 | RD | CCS Board A |  | J1 | CH 6 +
|  |  | CG-6 | I- | IC-1 | 24 | 235-05 | Belden 9546 |  | CR-TS-10 | 24-1 | 236-02 | Alpha 1896 | BK | CCS Board A |  | J1 | CH 6 -
12 | T_CL_P_C | 60-4K | CG-6_R | V+ | IC-2 | 22 | 235-05-R | Belden 9546 |  | CR-TS-10 | 22-2
| Redundant |  | CG-6_R | V- | IC-2 | 23 | 235-05-R | Belden 9546 |  | CR-TS-10 | 23-2
|  |  | CG-6_R | I+ | IC-2 | 21 | 235-05-R | Belden 9546 |  | CR-TS-10 | 21-2
|  |  | CG-6_R | I- | IC-2 | 24 | 235-05-R | Belden 9546 |  | CR-TS-10 | 24-2
13 | T_He_Resv | 60-4K | CG-7 | V+ | IC-B | 24 | 237-05 | Belden 9546 |  | CR-TS-10 | 26-1 | 236-03 | Alpha 1896 | WT | DF 1-6-3 | SCM5B30-02D | 1 | 19 | 236-07 | Alpha 6039C | WT | TS-PLC-06 | 7-1 | 306-01 | Belden 22676 | 4/WT | 1:I:6:CH 6 + | 1756-IF16 | T_He_Resv
|  |  | CG-7 | V- | IC-B | 25 | 237-05 | Belden 9546 |  | CR-TS-10 | 27-1 | 236-03 | Alpha 1896 | GN | DF 1-6-2 | SCM5B30-02D | 1 | 21 | 236-07 | Alpha 6039C | BK | TS-PLC-06 | 7-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  | CG-7 | I+ | IC-B | 23 | 237-05 | Belden 9546 |  | CR-TS-10 | 25-1 | 236-03 | Alpha 1896 | RD | CCS Board A |  | J1 | CH 7 +
|  |  | CG-7 | I- | IC-B | 26 | 237-05 | Belden 9546 |  | CR-TS-10 | 28-1 | 236-03 | Alpha 1896 | BK | CCS Board A |  | J1 | CH 7 -
14 | T_He_Resv | 60-4K | CG-7_R | V+ | IC-C | 24 | 237-05-R | Belden 9546 |  | CR-TS-10 | 26-2
| Redundant |  | CG-7_R | V- | IC-C | 25 | 237-05-R | Belden 9546 |  | CR-TS-10 | 27-2
|  |  | CG-7_R | I+ | IC-C | 23 | 237-05-R | Belden 9546 |  | CR-TS-10 | 25-2
|  |  | CG-7_R | I- | IC-C | 26 | 237-05-R | Belden 9546 |  | CR-TS-10 | 28-2
| SPARE | [15 empty] | 1 | 23 | 236-07 | Alpha 6039C | WT | TS-PLC-06 | 8-1 | 306-01 | Belden 22676 | 4/Bk | 1:I:6:CH 7 + | 1756-IF16 | SPARE
[17 empty] | 1 | 24 | 236-07 | Alpha 6039C | RD | TS-PLC-06 | 8-2 | 306-01 | Belden 22676 | JMPR | RTN
15 | TD_He_CoolDown | 350-4K | Diode-1 | V+ | IC-B | 8 | 237-05 | Belden 9546 |  | CR-TS-10 | 46-1 | 238-01 | Alpha 1896 | WT | DF 2-4-3 | SCM5B30-02D | 2 | 13 | 238-07 | Alpha 6039C | RD | TS-PLC-05 | 14-1 | 305-01 | Belden 22676 | 7/WT | 1:I:5:CH 12 + | 1756-IF16 | TD_He_CD
|  |  | Diode-1 | V- | IC-B | 9 | 237-05 | Belden 9546 |  | CR-TS-10 | 47-1 | 238-01 | Alpha 1896 | GN | DF 2-4-2 | SCM5B30-02D | 2 | 15 | 238-07 | Alpha 6039C | BK | TS-PLC-05 | 14-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | Diode-1 | I+ | IC-B | 7 | 237-05 | Belden 9546 |  | CR-TS-10 | 45-1 | 238-01 | Alpha 1896 | RD | CCS Board B |  | J1 | CH 1 +
|  |  | Diode-1 | I- | IC-B | 10 | 237-05 | Belden 9546 |  | CR-TS-10 | 48-1 | 238-01 | Alpha 1896 | BK | CCS Board B |  | J1 | CH 1 -
16 | TD_He_CoolDown | 350-4K | Diode-1_R | V+ | IC-C | 8 | 237-05_R | Belden 9546 |  | CR-TS-10 | 46-2
| Redundant |  | Diode-1_R | V- | IC-C | 9 | 237-05_R | Belden 9546 |  | CR-TS-10 | 47-2
|  |  | Diode-1_R | I+ | IC-C | 7 | 237-05_R | Belden 9546 |  | CR-TS-10 | 45-2
|  |  | Diode-1_R | I- | IC-C | 10 | 237-05_R | Belden 9546 |  | CR-TS-10 | 48-2
17 | TD_He_Supply | 350-4K | Diode-2 | V+ | IC-B | 12 | 237-05 | Belden 9546 |  | CR-TS-10 | 50-1 | 238-02 | Alpha 1896 | WT | DF 2-5-3 | SCM5B30-02D | 2 | 17 | 238-07 | Alpha 6039C | GN | TS-PLC-05 | 15-1 | 305-01 | Belden 22676 | 7/BK | 1:I:5:CH 13 + | 1756-IF16 | TD_He_Supply
|  |  | Diode-2 | V- | IC-B | 13 | 237-05 | Belden 9546 |  | CR-TS-10 | 51-1 | 238-02 | Alpha 1896 | GN | DF 2-5-2 | SCM5B30-02D | 2 | 18 | 238-07 | Alpha 6039C | BK | TS-PLC-05 | 15-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | Diode-2 | I+ | IC-B | 11 | 237-05 | Belden 9546 |  | CR-TS-10 | 49-1 | 238-02 | Alpha 1896 | RD | CCS Board B |  | J1 | CH 2 +
|  |  | Diode-2 | I- | IC-B | 14 | 237-05 | Belden 9546 |  | CR-TS-10 | 52-1 | 238-02 | Alpha 1896 | BK | CCS Board B |  | J1 | CH 2 -
18 | TD_He_Supply | 350-4K | Diode-2_R | V+ | IC-C | 12 | 237-05_R | Belden 9546 |  | CR-TS-10 | 50-2
| Redundant |  | Diode-2_R | V- | IC-C | 13 | 237-05_R | Belden 9546 |  | CR-TS-10 | 51-2
|  |  | Diode-2_R | I+ | IC-C | 11 | 237-05_R | Belden 9546 |  | CR-TS-10 | 49-2
|  |  | Diode-2_R | I- | IC-C | 14 | 237-05_R | Belden 9546 |  | CR-TS-10 | 52-2
19 | TD_He_Cold_Return | 350-4K | Diode-3 | V+ | IC-B | 16 | 237-05 | Belden 9546 |  | CR-TS-10 | 54-1 | 238-03 | Alpha 1896 | WT | DF 2-6-3 | SCM5B30-02D | 2 | 19 | 238-07 | Alpha 6039C | WT | TS-PLC-05 | 16-1 | 305-01 | Belden 22676 | 8/WT | 1:I:5:CH 14 + | 1756-IF16 | TD_He_CR
|  |  | Diode-3 | V- | IC-B | 17 | 237-05 | Belden 9546 |  | CR-TS-10 | 55-1 | 238-03 | Alpha 1896 | GN | DF 2-6-2 | SCM5B30-02D | 2 | 21 | 238-07 | Alpha 6039C | BK | TS-PLC-05 | 16-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | Diode-3 | I+ | IC-B | 15 | 237-05 | Belden 9546 |  | CR-TS-10 | 53-1 | 238-03 | Alpha 1896 | RD | CCS Board B |  | J1 | CH 3 +
|  |  | Diode-3 | I- | IC-B | 18 | 237-05 | Belden 9546 |  | CR-TS-10 | 56-1 | 238-03 | Alpha 1896 | BK | CCS Board B |  | J1 | CH 3 -
20 | TD_He_Cold_Return | 350-4K | Diode-3_R | V+ | IC-C | 16 | 237-05_R | Belden 9546 |  | CR-TS-10 | 54-2
| Redundant |  | Diode-3_R | V- | IC-C | 17 | 237-05_R | Belden 9546 |  | CR-TS-10 | 55-2
|  |  | Diode-3_R | I+ | IC-C | 15 | 237-05_R | Belden 9546 |  | CR-TS-10 | 53-2
|  |  | Diode-3_R | I- | IC-C | 18 | 237-05_R | Belden 9546 |  | CR-TS-10 | 56-2
21 | TD_Warm_Return | 350-4K | Diode-4 | V+ | IC-B | 20 | 237-05 | Belden 9546 |  | CR-TS-10 | 58-1 | 238-04 | Alpha 1896 | WT | DF 2-7 -3 | SCM5B30-02D | 2 | 23 | 238-07 | Alpha 6039C | WT | TS-PLC-05 | 17-1 | 305-01 | Belden 22676 | 8/BK | 1:I:5:CH 15 + | 1756-IF16 | TD_WR
|  |  | Diode-4 | V- | IC-B | 21 | 237-05 | Belden 9546 |  | CR-TS-10 | 59-1 | 238-04 | Alpha 1896 | GN | DF 2-7 -2 | SCM5B30-02D | 2 | 24 | 238-07 | Alpha 6039C | RD | TS-PLC-05 | 17-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | Diode-4 | I+ | IC-B | 19 | 237-05 | Belden 9546 |  | CR-TS-10 | 57-1 | 238-04 | Alpha 1896 | RD | CCS Board B |  | J1 | CH 4 +
|  |  | Diode-4 | I- | IC-B | 22 | 237-05 | Belden 9546 |  | CR-TS-10 | 60-1 | 238-04 | Alpha 1896 | BK | CCS Board B |  | J1 | CH 4 -
22 | TD_Warm_Return | 350-4K | Diode-4_R | V+ | IC-C | 20 | 237-05_R | Belden 9546 |  | CR-TS-10 | 58-2
| Redundant |  | Diode-4_R | V- | IC-C | 21 | 237-05_R | Belden 9546 |  | CR-TS-10 | 59-2
|  |  | Diode-4_R | I+ | IC-C | 19 | 237-05_R | Belden 9546 |  | CR-TS-10 | 57-2
|  |  | Diode-4_R | I- | IC-C | 22 | 237-05_R | Belden 9546 |  | CR-TS-10 | 60-2
23 | PT_Yoke_1 | 350-60 K | PT102-1 | M | IC-1 | 25 | 235-05 | Belden 9546 |  | CR-TS-10 | 61-1 | 239-01 | Alpha 1896 | RD | DF 3-0-4 | SCM5B34-1562 | 3 | 1 | 240-07 | Alpha 6039C | BL | TS-PLC-05 | 0-1 | 305-01 | Belden 22676 | 1/WT | 1:I:5:CH 0 + | 1756-IF16 | PT_Yoke_1
|  |  | PT102-1 | C | IC-1 | 26 | 235-05 | Belden 9546 |  | CR-TS-10 | 62-1 | 239-01 | Alpha 1896 | WT | DF 3-0-3 | SCM5B34-1562 | 3 | 3 | 240-07 | Alpha 6039C | BK | TS-PLC-05 | 0-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-1 | O | IC-1 | 27 | 235-05 | Belden 9546 |  | CR-TS-10 | 63-1 | 239-01 | Alpha 1896 | GN | DF 3-0-2 | SCM5B34-1562
[11 empty] | 64-1 | 239-01 | Alpha 1896 | BK | DF 3-0-1
24 | PT_Yoke_1 | 350-60 K | PT102-1_R | M | IC-2 | 25 | 235-05_R | Belden 9546 |  | CR-TS-10 | 61-2
| Redundant |  | PT102-1_R | C | IC-2 | 26 | 235-05_R | Belden 9546 |  | CR-TS-10 | 62-2
|  |  | PT102-1_R | O | IC-2 | 27 | 235-05_R | Belden 9546 |  | CR-TS-10 | 63-2
64-2
25 | PT_Yoke_2 | 350-60 K | PT102-2 | M | IC-1 | 28 | 235-05 | Belden 9546 |  | CR-TS-10 | 65-1 | 239-02 | Alpha 1896 | RD | DF 3-1-4 | SCM5B34-1562 | 3 | 5 | 240-07 | Alpha 6039C | YL | TS-PLC-05 | 1-1 | 305-01 | Belden 22676 | 1/BK | 1:I:5:CH 1 + | 1756-IF16 | PT_Yoke_2
|  |  | PT102-2 | C | IC-1 | 29 | 235-05 | Belden 9546 |  | CR-TS-10 | 66-1 | 239-02 | Alpha 1896 | WT | DF 3-1-3 | SCM5B34-1562 | 3 | 6 | 240-07 | Alpha 6039C | BK | TS-PLC-05 | 1-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-2 | O | IC-1 | 30 | 235-05 | Belden 9546 |  | CR-TS-10 | 67-1 | 239-02 | Alpha 1896 | GN | DF 3-1-2 | SCM5B34-1562
[11 empty] | 68-1 | 239-02 | Alpha 1896 | BK | DF 3-1-1
26 | PT_Yoke_2 | 350-60 K | PT102-2_R | M | IC-2 | 28 | 235-05_R | Belden 9546 |  | CR-TS-10 | 65-2
| Redundant |  | PT102-2_R | C | IC-2 | 29 | 235-05_R | Belden 9546 |  | CR-TS-10 | 66-2
|  |  | PT102-2_R | O | IC-2 | 30 | 235-05_R | Belden 9546 |  | CR-TS-10 | 67-2
68-2
27 | PT_Yoke_3 | 350-60 K | PT102-3 | M | IC-1 | 31 | 235-05 | Belden 9546 |  | CR-TS-10 | 69-1 | 239-03 | Alpha 1896 | RD | DF 3-2-4 | SCM5B34-1562 | 3 | 7 | 240-07 | Alpha 6039C | BN | TS-PLC-05 | 2-1 | 305-01 | Belden 22676 | 2/WT | 1:I:5:CH 2 + | 1756-IF16 | PT_Yoke_3
|  |  | PT102-3 | C | IC-1 | 32 | 235-05 | Belden 9546 |  | CR-TS-10 | 70-1 | 239-03 | Alpha 1896 | WT | DF 3-2-3 | SCM5B34-1562 | 3 | 9 | 240-07 | Alpha 6039C | BK | TS-PLC-05 | 2-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-3 | O | IC-1 | 33 | 235-05 | Belden 9546 |  | CR-TS-10 | 71-1 | 239-03 | Alpha 1896 | GN | DF 3-2-2 | SCM5B34-1562
[11 empty] | 72-1 | 239-03 | Alpha 1896 | BK | DF 3-2-1
28 | PT_Yoke_3 | 350-60 K | PT102-3_R | M | IC-2 | 31 | 235-05_R | Belden 9546 |  | CR-TS-10 | 69-2
| Redundant |  | PT102-3_R | C | IC-2 | 32 | 235-05_R | Belden 9546 |  | CR-TS-10 | 70-2
|  |  | PT102-3_R | O | IC-2 | 33 | 235-05_R | Belden 9546 |  | CR-TS-10 | 71-2
72-2
29 | PT_Yoke_4 | 350-60 K | PT102-4 | M | IC-1 | 34 | 235-05 | Belden 9546 |  | CR-TS-10 | 73-1 | 239-04 | Alpha 1896 | RD | DF 3-3-4 | SCM5B34-1562 | 3 | 11 | 240-07 | Alpha 6039C | OR | TS-PLC-05 | 3-1 | 305-01 | Belden 22676 | 2/BK | 1:I:5:CH 3 + | 1756-IF16 | PT_Yoke_4
|  |  | PT102-4 | C | IC-1 | 35 | 235-05 | Belden 9546 |  | CR-TS-10 | 74-1 | 239-04 | Alpha 1896 | WT | DF 3-3-3 | SCM5B34-1562 | 3 | 12 | 240-07 | Alpha 6039C | BK | TS-PLC-05 | 3-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-4 | O | IC-1 | 36 | 235-05 | Belden 9546 |  | CR-TS-10 | 75-1 | 239-04 | Alpha 1896 | GN | DF 3-3-2 | SCM5B34-1562
[11 empty] | 76-1 | 239-04 | Alpha 1896 | BK | DF 3-3-1
30 | PT_Yoke_4 | 350-60 K | PT102-4_R | M | IC-2 | 34 | 235-05_R | Belden 9546 |  | CR-TS-10 | 73-2
| Redundant |  | PT102-4_R | C | IC-2 | 35 | 235-05_R | Belden 9546 |  | CR-TS-10 | 74-2
|  |  | PT102-4_R | O | IC-2 | 36 | 235-05_R | Belden 9546 |  | CR-TS-10 | 75-2
76-2
31 | PT_N2_IN | 350-60 K | PT102-5 | M | IC-B | 1 | 237-05 | Belden 9546 |  | CR-TS-10 | 29-1 | 237-01 | Alpha 1896 | RD | DF 2-0-4 | SCM5B34-1562 | 2 | 1 | 238-07 | Alpha 6039C | BL | TS-PLC-05 | 9-1 | 305-01 | Belden 22676 | 5/WT | 1:I:5:CH 8 + | 1756-IF16 | PT_N2_IN
|  |  | PT102-5 | C | IC-B | 2 | 237-05 | Belden 9546 |  | CR-TS-10 | 30-1 | 237-01 | Alpha 1896 | WT | DF 2-0-3 | SCM5B34-1562 | 2 | 3 | 238-07 | Alpha 6039C | BK | TS-PLC-05 | 9-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-5 | O | IC-B | 3 | 237-05 | Belden 9546 |  | CR-TS-10 | 31-1 | 237-01 | Alpha 1896 | GN | DF 2-0-2 | SCM5B34-1562
[11 empty] | 32-1 | 237-01 | Alpha 1896 | BK | DF 2-0-1
32 | PT_N2_IN | 350-60 K | PT102-5_R | M | IC-C | 1 | 237-05_R | Belden 9546 |  | CR-TS-10 | 29-2
| Redundant |  | PT102-5_R | C | IC-C | 2 | 237-05_R | Belden 9546 |  | CR-TS-10 | 30-2
|  |  | PT102-5_R | O | IC-C | 3 | 237-05_R | Belden 9546 |  | CR-TS-10 | 31-2
32-2
33 | PT_N2_Return | 350-60 K | PT102-10 | M | IC-B | 4 | 237-05 | Belden 9546 |  | CR-TS-10 | 33-1 | 237-02 | Alpha 1896 | RD | DF 2-1-4 | SCM5B34-1562 | 2 | 5 | 238-07 | Alpha 6039C | YL | TS-PLC-05 | 10-1 | 305-01 | Belden 22676 | 5/BK | 1:I:5:CH 9 + | 1756-IF16 | PT_N2_Return
|  |  | PT102-10 | C | IC-B | 5 | 237-05 | Belden 9546 |  | CR-TS-10 | 34-1 | 237-02 | Alpha 1896 | WT | DF 2-1-3 | SCM5B34-1562 | 2 | 6 | 238-07 | Alpha 6039C | BK | TS-PLC-05 | 10-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-10 | O | IC-B | 6 | 237-05 | Belden 9546 |  | CR-TS-10 | 35-1 | 237-02 | Alpha 1896 | GN | DF 2-1-2 | SCM5B34-1562
[11 empty] | 36-1 | 237-02 | Alpha 1896 | BK | DF 2-1-1
34 | PT_N2_Return | 350-60 K | PT102-10_R | M | IC-C | 4 | 237-05_R | Belden 9546 |  | CR-TS-10 | 33-2
| Redundant |  | PT102-10_R | C | IC-C | 5 | 237-05_R | Belden 9546 |  | CR-TS-10 | 34-2
|  |  | PT102-10_R | O | IC-C | 6 | 237-05_R | Belden 9546 |  | CR-TS-10 | 35-2
36-2
35 | PT_CL_N_Warm | 350-60 K | PT102-11 | M |  | 1 | 237-06 |  |  | CR-TS-10 | 37-1 | 237-03 | Alpha 1896 | RD | DF 2-2-4 | SCM5B34-1562 | 2 | 7 | 238-07 | Alpha 6039C | BN | TS-PLC-05 | 11-1 | 305-01 | Belden 22676 | 6/WT | 1:I:5:CH 10 + | 1756-IF16 | PT_CL_N_Warm
|  |  | PT102-11 | C |  | 2 | 237-06 |  |  | CR-TS-10 | 38-1 | 237-03 | Alpha 1896 | WT | DF 2-2-3 | SCM5B34-1562 | 2 | 9 | 238-07 | Alpha 6039C | BK | TS-PLC-05 | 11-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-11 | O |  | 3 | 237-06 |  |  | CR-TS-10 | 39-1 | 237-03 | Alpha 1896 | GN | DF 2-2-2 | SCM5B34-1562
[11 empty] | 40-1 | 237-03 | Alpha 1896 | BK | DF 2-2-1
36 | PT_CL_P_Warm | 350-60 K | PT102-12 | M |  | 1 | 237-07 |  |  | CR-TS-10 | 41-1 | 237-04 | Alpha 1896 | RD | DF 2-3-4 | SCM5B34-1562 | 2 | 11 | 238-07 | Alpha 6039C | OR | TS-PLC-05 | 12-1 | 305-01 | Belden 22676 | 6/Bk | 1:I:5:CH 11 + | 1756-IF16 | PT_CL_P_Warm
|  |  | PT102-12 | C |  | 2 | 237-07 |  |  | CR-TS-10 | 42-1 | 237-04 | Alpha 1896 | WT | DF 2-3-3 | SCM5B34-1562 | 2 | 12 | 238-07 | Alpha 6039C | BK | TS-PLC-05 | 12-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-12 | O |  | 3 | 237-07 |  |  | CR-TS-10 | 43-1 | 237-04 | Alpha 1896 | GN | DF 2-3-2 | SCM5B34-1562
[11 empty] | 44-1 | 237-04 | Alpha 1896 | BK | DF 2-3-1
37 | PT_N2_Outer_Top | 350-60 K | PT102-6 | M | IC-A | 1 | 240-05 | Belden 9546 |  | CR-TS-10 | 77-1 | 240-01 | Alpha 1896 | RD | DF 3-4-4 | SCM5B34-1562 | 3 | 13 | 240-07 | Alpha 6039C | RD | TS-PLC-05 | 5-1 | 305-01 | Belden 22676 | 3/WT | 1:I:5:CH 4 + | 1756-IF16 | PT_N2_OT
|  |  | PT102-6 | C | IC-A | 2 | 240-05 | Belden 9546 |  | CR-TS-10 | 78-1 | 240-01 | Alpha 1896 | WT | DF 3-4-3 | SCM5B34-1562 | 3 | 15 | 240-07 | Alpha 6039C | BK | TS-PLC-05 | 5-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-6 | O | IC-A | 3 | 240-05 | Belden 9546 |  | CR-TS-10 | 79-1 | 240-01 | Alpha 1896 | GN | DF 3-4-2 | SCM5B34-1562
[11 empty] | 80-1 | 240-01 | Alpha 1896 | BK | DF 3-4-1
38 | PT_N2_Outer_Top | 350-60 K | PT102-6_R | M | IC-A | 13 | 240-05 | Belden 9546 |  | CR-TS-10 | 77-2
| Redundant |  | PT102-6_R | C | IC-A | 14 | 240-05 | Belden 9546 |  | CR-TS-10 | 78-2
|  |  | PT102-6_R | O | IC-A | 15 | 240-05 | Belden 9546 |  | CR-TS-10 | 79-2
80-2
39 | PT_N2_Outer_Bottom | 350-60 K | PT102-7 | M | IC-A | 4 | 240-05 | Belden 9546 |  | CR-TS-10 | 81-1 | 240-02 | Alpha 1896 | RD | DF 3-5-4 | SCM5B34-1562 | 3 | 17 | 240-07 | Alpha 6039C | GN | TS-PLC-05 | 6-1 | 305-01 | Belden 22676 | 3/BK | 1:I:5:CH 5 + | 1756-IF16 | PT_N2_OB
|  |  | PT102-7 | C | IC-A | 5 | 240-05 | Belden 9546 |  | CR-TS-10 | 82-1 | 240-02 | Alpha 1896 | WT | DF 3-5-3 | SCM5B34-1562 | 3 | 18 | 240-07 | Alpha 6039C | BK | TS-PLC-05 | 6-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-7 | O | IC-A | 6 | 240-05 | Belden 9546 |  | CR-TS-10 | 83-1 | 240-02 | Alpha 1896 | GN | DF 3-5-2 | SCM5B34-1562
[11 empty] | 84-1 | 240-02 | Alpha 1896 | BK | DF 3-5-1
40 | PT_N2_Outer_Bottom | 350-60 K | PT102-7_R | M | IC-A | 16 | 240-05 | Belden 9546 |  | CR-TS-10 | 81-2
| Redundant |  | PT102-7_R | C | IC-A | 17 | 240-05 | Belden 9546 |  | CR-TS-10 | 82-2
|  |  | PT102-7_R | O | IC-A | 18 | 240-05 | Belden 9546 |  | CR-TS-10 | 83-2
84-2
41 | PT_N2_Bore_Top | 350-60 K | PT102-8 | M | IC-A | 7 | 240-05 | Belden 9546 |  | CR-TS-10 | 85-1 | 240-03 | Alpha 1896 | RD | DF 3-6-4 | SCM5B34-1562 | 3 | 19 | 240-07 | Alpha 6039C | WT | TS-PLC-05 | 7-1 | 305-01 | Belden 22676 | 4/WT | 1:I:5:CH 6 + | 1756-IF16 | PT_N2_BT
|  |  | PT102-8 | C | IC-A | 8 | 240-05 | Belden 9546 |  | CR-TS-10 | 86-1 | 240-03 | Alpha 1896 | WT | DF 3-6-3 | SCM5B34-1562 | 3 | 21 | 240-07 | Alpha 6039C | BK | TS-PLC-05 | 7-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-8 | O | IC-A | 9 | 240-05 | Belden 9546 |  | CR-TS-10 | 87-1 | 240-03 | Alpha 1896 | GN | DF 3-6-2 | SCM5B34-1562
[11 empty] | 88-1 | 240-03 | Alpha 1896 | BK | DF 3-6-1
42 | PT_N2_Bore_Top | 350-60 K | PT102-8_R | M | IC-A | 19 | 240-05 | Belden 9546 |  | CR-TS-10 | 85-2
| Redundant |  | PT102-8_R | C | IC-A | 20 | 240-05 | Belden 9546 |  | CR-TS-10 | 86-2
|  |  | PT102-8_R | O | IC-A | 21 | 240-05 | Belden 9546 |  | CR-TS-10 | 87-2
88-2
43 | PT_N2_Bore_Bottom | 350-60 K | PT102-9 | M | IC-A | 10 | 240-05 | Belden 9546 |  | CR-TS-10 | 89-1 | 240-04 | Alpha 1896 | RD | DF 3-7-4 | SCM5B34-1562 | 3 | 23 | 240-07 | Alpha 6039C | WT | TS-PLC-05 | 8-1 | 305-01 | Belden 22676 | 4/BK | 1:I:5:CH 7 + | 1756-IF16 | PT_N2_BB
|  |  | PT102-9 | C | IC-A | 11 | 240-05 | Belden 9546 |  | CR-TS-10 | 90-1 | 240-04 | Alpha 1896 | WT | DF 3-7-3 | SCM5B34-1562 | 3 | 24 | 240-07 | Alpha 6039C | RD | TS-PLC-05 | 8-2 | 305-01 | Belden 22676 | JMPR | RTN
|  |  | PT102-9 | O | IC-A | 12 | 240-05 | Belden 9546 |  | CR-TS-10 | 91-1 | 240-04 | Alpha 1896 | GN | DF 3-7-2 | SCM5B34-1562
[11 empty] | 92-1 | 240-04 | Alpha 1896 | BK | DF 3-7-1
44 | PT_N2_Bore_Bottom | 350-60 K | PT102-9_R | M | IC-A | 22 | 240-05 | Belden 9546 |  | CR-TS-10 | 89-2
| Redundant |  | PT102-9_R | C | IC-A | 23 | 240-05 | Belden 9546 |  | CR-TS-10 | 90-2
|  |  | PT102-9_R | O | IC-A | 24 | 240-05 | Belden 9546 |  | CR-TS-10 | 91-2
92-2
Strain Gauges
45 | SG_1 | 350-0 kN | SG1/1 | P- | SG-A | 1 | 255-05 | Belden 9538 |  | CR_TS-11 | 4-1 | 255-01 | Alpha 1896 | BK | DF 5-0-1 | SCM5B38-35D | 5 | 1 | 256-10 | Alpha 6039C | BL | TS-PLC-07 | 0-1 | 307-01 | Belden 22676 | 1/WT | 1:I:7:CH 0 + | 1756-IF16 | SG_1
|  |  | SG1/1 | S- | SG-A | 2 | 255-05 | Belden 9538 |  | CR_TS-11 | 3-1 | 255-01 | Alpha 1896 | GN | DF 5-0-2 | SCM5B38-35D | 5 | 3 | 256-10 | Alpha 6039C | BK | TS-PLC-07 | 0-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG1/1 | S+ | SG-A | 3 | 255-05 | Belden 9538 |  | CR_TS-11 | 2-1 | 255-01 | Alpha 1896 | WT | DF 5-0-3 | SCM5B38-35D
|  |  | SG1/1 | P+ | SG-A | 4 | 255-05 | Belden 9538 |  | CR_TS-11 | 1-1 | 255-01 | Alpha 1896 | RD | DF 5-0-4 | SCM5B38-35D
46 | SG_1 | 350-0 kN | SG1/2 | P- | SG-A | 5 | 255-05 | Belden 9538 |  | CR_TS-11 | 4-2
| Redundant |  | SG1/2 | S- | SG-A | 6 | 255-05 | Belden 9538 |  | CR_TS-11 | 3-2
|  |  | SG1/2 | S+ | SG-A | 8 | 255-05 | Belden 9538 |  | CR_TS-11 | 2-2
|  |  | SG1/2 | P+ | SG-A | 7 | 255-05 | Belden 9538 |  | CR_TS-11 | 1-2
47 | SG_2 | 350-0 kN | SG2/1 | P- | SG-B | 1 | 255-06 | Belden 9538 |  | CR_TS-11 | 8-1 | 255-02 | Alpha 1896 | BK | DF 5-1-1 | SCM5B38-35D | 5 | 5 | 256-10 | Alpha 6039C | YL | TS-PLC-07 | 1-1 | 307-01 | Belden 22676 | 1/BK | 1:I:7:CH 1 + | 1756-IF16 | SG_2
|  |  | SG2/1 | S- | SG-B | 2 | 255-06 | Belden 9538 |  | CR_TS-11 | 7-1 | 255-02 | Alpha 1896 | GN | DF 5-1-2 | SCM5B38-35D | 5 | 6 | 256-10 | Alpha 6039C | BK | TS-PLC-07 | 1-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG2/1 | S+ | SG-B | 3 | 255-06 | Belden 9538 |  | CR_TS-11 | 6-1 | 255-02 | Alpha 1896 | WT | DF 5-1-3 | SCM5B38-35D
|  |  | SG2/1 | P+ | SG-B | 4 | 255-06 | Belden 9538 |  | CR_TS-11 | 5-1 | 255-02 | Alpha 1896 | RD | DF 5-1-4 | SCM5B38-35D
48 | SG_2 | 350-0 kN | SG2/2 | P- | SG-B | 5 | 255-06 | Belden 9538 |  | CR_TS-11 | 8-2
| Redundant |  | SG2/2 | S- | SG-B | 6 | 255-06 | Belden 9538 |  | CR_TS-11 | 7-2
|  |  | SG2/2 | S+ | SG-B | 8 | 255-06 | Belden 9538 |  | CR_TS-11 | 6-2
|  |  | SG2/2 | P+ | SG-B | 7 | 255-06 | Belden 9538 |  | CR_TS-11 | 5-2
49 | SG_3 | 350-0 kN | SG3/1 | P- | SG-C | 1 | 255-07 | Belden 9538 |  | CR_TS-11 | 12-1 | 255-03 | Alpha 1896 | BK | DF 5-2-1 | SCM5B38-35D | 5 | 7 | 256-10 | Alpha 6039C | BN | TS-PLC-07 | 2-1 | 307-01 | Belden 22676 | 2/WT | 1:I:7:CH 2 + | 1756-IF16 | SG_3
|  |  | SG3/1 | S- | SG-C | 2 | 255-07 | Belden 9538 |  | CR_TS-11 | 11-1 | 255-03 | Alpha 1896 | GN | DF 5-2-2 | SCM5B38-35D | 5 | 9 | 256-10 | Alpha 6039C | BK | TS-PLC-07 | 2-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG3/1 | S+ | SG-C | 3 | 255-07 | Belden 9538 |  | CR_TS-11 | 10-1 | 255-03 | Alpha 1896 | WT | DF 5-2-3 | SCM5B38-35D
|  |  | SG3/1 | P+ | SG-C | 4 | 255-07 | Belden 9538 |  | CR_TS-11 | 9-1 | 255-03 | Alpha 1896 | RD | DF 5-2-4 | SCM5B38-35D
50 | SG_3 | 350-0 kN | SG3/2 | P- | SG-C | 5 | 255-07 | Belden 9538 |  | CR_TS-11 | 12-2
| Redundant |  | SG3/2 | S- | SG-C | 6 | 255-07 | Belden 9538 |  | CR_TS-11 | 11-2
|  |  | SG3/2 | S+ | SG-C | 8 | 255-07 | Belden 9538 |  | CR_TS-11 | 10-2
|  |  | SG3/2 | P+ | SG-C | 7 | 255-07 | Belden 9538 |  | CR_TS-11 | 9-2
51 | SG_4 | 350-0 kN | SG4/1 | P- | SG-D | 1 | 255-08 | Belden 9538 |  | CR_TS-11 | 16-1 | 255-04 | Alpha 1896 | BK | DF 5-3-1 | SCM5B38-35D | 5 | 11 | 256-10 | Alpha 6039C | OR | TS-PLC-07 | 3-1 | 307-01 | Belden 22676 | 2/BK | 1:I:7:CH 3 + | 1756-IF16 | SG_4
|  |  | SG4/1 | S- | SG-D | 2 | 255-08 | Belden 9538 |  | CR_TS-11 | 15-1 | 255-04 | Alpha 1896 | GN | DF 5-3-2 | SCM5B38-35D | 5 | 12 | 256-10 | Alpha 6039C | BK | TS-PLC-07 | 3-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG4/1 | S+ | SG-D | 3 | 255-08 | Belden 9538 |  | CR_TS-11 | 14-1 | 255-04 | Alpha 1896 | WT | DF 5-3-3 | SCM5B38-35D
|  |  | SG4/1 | P+ | SG-D | 4 | 255-08 | Belden 9538 |  | CR_TS-11 | 13-1 | 255-04 | Alpha 1896 | RD | DF 5-3-4 | SCM5B38-35D
52 | SG_4 | 350-0 kN | SG4/2 | P- | SG-D | 5 | 255-08 | Belden 9538 |  | CR_TS-11 | 16-2
| Redundant |  | SG4/2 | S- | SG-D | 6 | 255-08 | Belden 9538 |  | CR_TS-11 | 15-2
|  |  | SG4/2 | S+ | SG-D | 8 | 255-08 | Belden 9538 |  | CR_TS-11 | 14-2
|  |  | SG4/2 | P+ | SG-D | 7 | 255-08 | Belden 9538 |  | CR_TS-11 | 13-2
53 | SG_5 | 350-0 kN | SG5/1 | P- | SG-E | 1 | 256-05 | Belden 9538 |  | CR_TS-11 | 20-1 | 256-01 | Alpha 1896 | BK | DF 5-4-1 | SCM5B38-35D | 5 | 13 | 256-10 | Alpha 6039C | RD | TS-PLC-07 | 5-1 | 307-01 | Belden 22676 | 3/WT | 1:I:7:CH 4 + | 1756-IF16 | SG_5
|  |  | SG5/1 | S- | SG-E | 2 | 256-05 | Belden 9538 |  | CR_TS-11 | 19-1 | 256-01 | Alpha 1896 | GN | DF 5-4-2 | SCM5B38-35D | 5 | 15 | 256-10 | Alpha 6039C | BK | TS-PLC-07 | 5-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG5/1 | S+ | SG-E | 3 | 256-05 | Belden 9538 |  | CR_TS-11 | 18-1 | 256-01 | Alpha 1896 | WT | DF 5-4-3 | SCM5B38-35D
|  |  | SG5/1 | P+ | SG-E | 4 | 256-05 | Belden 9538 |  | CR_TS-11 | 17-1 | 256-01 | Alpha 1896 | RD | DF 5-4-4 | SCM5B38-35D
54 | SG_5 | 350-0 kN | SG5/2 | P- | SG-E | 5 | 256-05 | Belden 9538 |  | CR_TS-11 | 20-2
| Redundant |  | SG5/2 | S- | SG-E | 6 | 256-05 | Belden 9538 |  | CR_TS-11 | 19-2
|  |  | SG5/2 | S+ | SG-E | 8 | 256-05 | Belden 9538 |  | CR_TS-11 | 18-2
|  |  | SG5/2 | P+ | SG-E | 7 | 256-05 | Belden 9538 |  | CR_TS-11 | 17-2
55 | SG_6 | 350-0 kN | SG6/1 | P- | SG-F | 1 | 256-06 | Belden 9538 |  | CR_TS-11 | 24-1 | 256-02 | Alpha 1896 | BK | DF 5-5-1 | SCM5B38-35D | 5 | 17 | 256-10 | Alpha 6039C | GN | TS-PLC-07 | 6-1 | 307-01 | Belden 22676 | 3/BK | 1:I:7:CH 5 + | 1756-IF16 | SG_6
|  |  | SG6/1 | S- | SG-F | 2 | 256-06 | Belden 9538 |  | CR_TS-11 | 23-1 | 256-02 | Alpha 1896 | GN | DF 5-5-2 | SCM5B38-35D | 5 | 18 | 256-10 | Alpha 6039C | BK | TS-PLC-07 | 6-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG6/1 | S+ | SG-F | 3 | 256-06 | Belden 9538 |  | CR_TS-11 | 22-1 | 256-02 | Alpha 1896 | WT | DF 5-5-3 | SCM5B38-35D
|  |  | SG6/1 | P+ | SG-F | 4 | 256-06 | Belden 9538 |  | CR_TS-11 | 21-1 | 256-02 | Alpha 1896 | RD | DF 5-5-4 | SCM5B38-35D
56 | SG_6 | 350-0 kN | SG6/2 | P- | SG-F | 5 | 256-06 | Belden 9538 |  | CR_TS-11 | 24-2
| Redundant |  | SG6/2 | S- | SG-F | 6 | 256-06 | Belden 9538 |  | CR_TS-11 | 23-2
|  |  | SG6/2 | S+ | SG-F | 8 | 256-06 | Belden 9538 |  | CR_TS-11 | 22-2
|  |  | SG6/2 | P+ | SG-F | 7 | 256-06 | Belden 9538 |  | CR_TS-11 | 21-2
57 | SG_7 | 350-0 kN | SG7/1 | P- | SG-G | 1 | 256-07 | Belden 9538 |  | CR_TS-11 | 28-1 | 256-03 | Alpha 1896 | BK | DF 5-6-1 | SCM5B38-35D | 5 | 19 | 256-10 | Alpha 6039C | WT | TS-PLC-07 | 7-1 | 307-01 | Belden 22676 | 4/WT | 1:I:7:CH 6 + | 1756-IF16 | SG_7
|  |  | SG7/1 | S- | SG-G | 2 | 256-07 | Belden 9538 |  | CR_TS-11 | 27-1 | 256-03 | Alpha 1896 | GN | DF 5-6-2 | SCM5B38-35D | 5 | 21 | 256-10 | Alpha 6039C | BK | TS-PLC-07 | 7-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG7/1 | S+ | SG-G | 3 | 256-07 | Belden 9538 |  | CR_TS-11 | 26-1 | 256-03 | Alpha 1896 | WT | DF 5-6-3 | SCM5B38-35D
|  |  | SG7/1 | P+ | SG-G | 4 | 256-07 | Belden 9538 |  | CR_TS-11 | 25-1 | 256-03 | Alpha 1896 | RD | DF 5-6-4 | SCM5B38-35D
58 | SG_7 | 350-0 kN | SG7/2 | P- | SG-G | 5 | 256-07 | Belden 9538 |  | CR_TS-11 | 28-2
| Redundant |  | SG7/2 | S- | SG-G | 6 | 256-07 | Belden 9538 |  | CR_TS-11 | 27-2
|  |  | SG7/2 | S+ | SG-G | 8 | 256-07 | Belden 9538 |  | CR_TS-11 | 26-2
|  |  | SG7/2 | P+ | SG-G | 7 | 256-07 | Belden 9538 |  | CR_TS-11 | 25-2
59 | SG_8 | 350-0 kN | SG8/1 | P- | SG-H | 1 | 256-08 | Belden 9538 |  | CR_TS-11 | 32-1 | 256-04 | Alpha 1896 | BK | DF 5-7-1 | SCM5B38-35D | 5 | 23 | 256-10 | Alpha 6039C | WT | TS-PLC-07 | 8-1 | 307-01 | Belden 22676 | 4/BK | 1:I:7:CH 7 + | 1756-IF16 | SG_8
|  |  | SG8/1 | S- | SG-H | 2 | 256-08 | Belden 9538 |  | CR_TS-11 | 31-1 | 256-04 | Alpha 1896 | GN | DF 5-7-2 | SCM5B38-35D | 5 | 24 | 256-10 | Alpha 6039C | RD | TS-PLC-07 | 8-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG8/1 | S+ | SG-H | 3 | 256-08 | Belden 9538 |  | CR_TS-11 | 30-1 | 256-04 | Alpha 1896 | WT | DF 5-7-3 | SCM5B38-35D
|  |  | SG8/1 | P+ | SG-H | 4 | 256-08 | Belden 9538 |  | CR_TS-11 | 29-1 | 256-04 | Alpha 1896 | RD | DF 5-7-4 | SCM5B38-35D
60 | SG_8 | 350-0 kN | SG8/2 | P- | SG-H | 5 | 256-08 | Belden 9538 |  | CR_TS-11 | 32-2
| Redundant |  | SG8/2 | S- | SG-H | 6 | 256-08 | Belden 9538 |  | CR_TS-11 | 31-2
|  |  | SG8/2 | S+ | SG-H | 8 | 256-08 | Belden 9538 |  | CR_TS-11 | 30-2
|  |  | SG8/2 | P+ | SG-H | 7 | 256-08 | Belden 9538 |  | CR_TS-11 | 29-2
Bender Strain Gauges
61 | SG_9 | 350-0 kN | SG9/1 | P- | SG-I | 1 | 261-1-08 | Belden 9538 |  | CR_TS-11 | 36-1 | 261-1-02 | Alpha 1896 | BK | DF 6-6-1 | SCM5B38-35D | 6 | 19 | 256-10 | Belden 22676 | 9/WT | TS-PLC-07 | 9-1 | 307-01 | Belden 22676 | 5/WT | 1:I:7:CH 8 + | 1756-IF16 | SG_9
|  |  | SG9/1 | S- | SG-I | 2 | 261-1-08 | Belden 9538 |  | CR_TS-11 | 35-1 | 261-1-02 | Alpha 1896 | GN | DF 6-6-2 | SCM5B38-35D | 6 | 21 | 256-10 | Belden 22676 | 9/BK | TS-PLC-07 | 9-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG9/1 | S+ | SG-I | 3 | 261-1-08 | Belden 9538 |  | CR_TS-11 | 34-1 | 261-1-02 | Alpha 1896 | WT | DF 6-6-3 | SCM5B38-35D
|  |  | SG9/1 | P+ | SG-I | 4 | 261-1-08 | Belden 9538 |  | CR_TS-11 | 33-1 | 261-1-02 | Alpha 1896 | RD | DF 6-6-4 | SCM5B38-35D
62 | SG_9 | 350-0 kN | SG9/2 | P- | SG-I | 5 | 261-1-08 | Belden 9538 |  | CR_TS-11 | 36-2
| Redundant |  | SG9/2 | S- | SG-I | 6 | 261-1-08 | Belden 9538 |  | CR_TS-11 | 35-2
|  |  | SG9/2 | S+ | SG-I | 8 | 261-1-08 | Belden 9538 |  | CR_TS-11 | 34-2
|  |  | SG9/2 | P+ | SG-I | 7 | 261-1-08 | Belden 9538 |  | CR_TS-11 | 33-2
63 | SG_10 | 350-0 kN | SG10/1 | P- | SG-J | 1 | 261-1-09 | Belden 9538 |  | CR_TS-11 | 40-1 | 261-1-03 | Alpha 1896 | BK | DF 6-7-1 | SCM5B38-35D | 6 | 23 | 256-10 | Belden 22676 | 10/WT | TS-PLC-07 | 10-1 | 307-01 | Belden 22676 | 5/BK | 1:I:7:CH 9 + | 1756-IF16 | SG_10
|  |  | SG10/1 | S- | SG-J | 2 | 261-1-09 | Belden 9538 |  | CR_TS-11 | 39-1 | 261-1-03 | Alpha 1896 | GN | DF 6-7-2 | SCM5B38-35D | 6 | 24 | 256-10 | Belden 22676 | 10/BK | TS-PLC-07 | 10-2 | 307-01 | Belden 22676 | JMPR | RTN
|  |  | SG10/1 | S+ | SG-J | 3 | 261-1-09 | Belden 9538 |  | CR_TS-11 | 38-1 | 261-1-03 | Alpha 1896 | WT | DF 6-7-3 | SCM5B38-35D
|  |  | SG10/1 | P+ | SG-J | 4 | 261-1-09 | Belden 9538 |  | CR_TS-11 | 37-1 | 261-1-03 | Alpha 1896 | RD | DF 6-7-4 | SCM5B38-35D
64 | SG_10 | 350-0 kN | SG10/2 | P- | SG-J | 5 | 261-1-09 | Belden 9538 |  | CR_TS-11 | 40-2
| Redundant |  | SG10/2 | S- | SG-J | 6 | 261-1-09 | Belden 9538 |  | CR_TS-11 | 39-2
|  |  | SG10/2 | S+ | SG-J | 8 | 261-1-09 | Belden 9538 |  | CR_TS-11 | 38-2
|  |  | SG10/2 | P+ | SG-J | 7 | 261-1-09 | Belden 9538 |  | CR_TS-11 | 37-2
| Voltage Taps | Range | Sensor |  | Connector | Connector | Cable | Cable | Wire | Pot Tap | Cable | Cable | Wire | Term Strip | Pin | Cable | Wire | Signal |  | Pin connection | DataForth | Pin | Cable Type | wire color |  | Term Strip | Pin | PLC | wire color | I/O Module | I/O Module | PLC
|  |  | Name |  |  | Pin # | Label | Type | Color | Resistor Box | Label |  | Color |  |  |  | Color | Conditioner |  |  | SCMXIF-DIN | Out | Cable Label |  |  |  | Row-block | Cable |  | Channel | Type | Tag Name
Pin
| DC 1 | - | Broken Wire Sensor |  | Resistor Panel | 1 | 260-1-00 |  |  | 1 | 260-1-05 |  |  | CR-TS-13
| DC 2 | - | Broken Wire Sensor |  | Resistor Panel | 2 | 260-1-00 |  |  | 2 | 260-1-05 |  |  | CR-TS-13
65 | Pot Tap 1+U |  | CL-L_warm |  | Resistor Panel | 3 | 260-1-00 |  |  | 3 | 260-1-05 |  |  | CR-TS-13 | 1 | 265-1-01 |  | Quench Detector |  | D1H & D1L
| Pot Tap 1+U |  | CL-L_warm |  | Resistor Panel | 3 | 260-1-00 |  |  | 3 | 260-1-05 |  |  | CR-TS-13 | 2 | 260-1-01 | wt | SCM5B31-09D |  | DF 6-0-3 | 6 | 1 | 261-1-06 | 1/wt |  | TS-PLC-09 | 0-1 | 309-01 | 1/wt | 1:I:9:CH 0 + | 1756-IF16 | CL_L
66 | Pot Tap 1-U |  | CL-R_warm |  | Resistor Panel | 4 | 260-1-00 |  |  | 4 | 260-1-05 |  |  | CR-TS-13 | 30 | 265-1-01 |  | Quench Detector |  | D4LM & D4HM
| Pot Tap 1-U |  | CL-R_warm |  | Resistor Panel | 4 | 260-1-00 |  |  | 4 | 260-1-05 |  |  | CR-TS-13 | 31 | 261-1-01 | bk | SCM5B31-09D |  | DF 6-5-2 | 6 | 18 | 261-1-06 | 6/bk |  | TS-PLC-09 | 12-1 | 309-01 | 6/bk | 1:I:9:CH 5 - | 1756-IF16 | CL_R
67 | Pot Tap 1+U R |  | CL-L_warm_R |  | Resistor Panel | 5 | 260-1-00 |  |  | 5 | 260-1-05 |  |  | CR-TS-13 | 5
| Pot Tap 1+U R |  | CL-L_warm_R |  | Resistor Panel | 5 | 260-1-00 |  |  | 5 | 260-1-05 |  |  | CR-TS-13 | 6
68 | Pot Tap 1-U R |  | CL-R-warm_R |  | Resistor Panel | 6 | 260-1-00 |  |  | 6 | 260-1-05 |  |  | CR-TS-13 | 34
| Pot Tap 1-U R |  | CL-R-warm_R |  | Resistor Panel | 6 | 260-1-00 |  |  | 6 | 260-1-05 |  |  | CR-TS-13 | 35
69 | Pot Tap I+M1 |  |  |  | IC-3 | 1 | 260-1-06 |  |  | 7 | 260-1-05 |  |  | CR-TS-12 | 1-1
70 | Pot Tap I+M2 |  |  |  | IC-3 | 2 | 260-1-06 |  |  | 8 | 260-1-05 |  |  | CR-TS-12 | 2-1
71 | Pot Tap I+L1 |  |  |  | IC-3 | 3 | 260-1-06 |  |  | 9 | 260-1-05 |  |  | CR-TS-13 | 10 | 265-1-01 |  | Quench Detector |  | D2H
| Pot Tap I+L1 |  |  |  | IC-3 | 3 | 260-1-06 |  |  | 9 | 260-1-05 |  |  | CR-TS-13 | 11 | 260-1-01 | wt | SCM5B31-09D |  | DF 6-1-3 | 6 | 6 | 261-1-06 | 2/bk |  | TS-PLC-09 | 3-1 | 309-01 | 2/bk | 1:I:9:CH 1 - | 1756-IF16 | Coil 1
72 | Pot Tap I+L2 |  |  |  | IC-3 | 4 | 260-1-06 |  |  | 10 | 260-1-05 |  |  | CR-TS-13 | 4 | 265-1-01 |  | Quench Detector |  | D1LM & D1HM
| Pot Tap I+L2 |  |  |  | IC-3 | 4 | 260-1-06 |  |  | 10 | 260-1-05 |  |  | CR-TS-13 | 3 | 261-1-01 | bk | SCM5B31-09D |  | DF 6-0-2 | 6 | 3 | 261-1-06 | 1/bk |  | TS-PLC-09 | 1-1 | 309-01 | 1/bk | 1:I:9:CH 0 - | 1756-IF16 | CL_L
73 | Pot Tap 1/1B |  |  |  | IC-3 | 5 | 260-1-06 |  |  | 11 | 260-1-05 |  |  | CR-TS-13 | 19 | 265-1-01 |  | Quench Detector |  | D2LM
| Pot Tap 1/1B |  |  |  | IC-3 | 5 | 260-1-06 |  |  | 11 | 260-1-05 |  |  | CR-TS-13 | 20 | 260-1-01 | wt | SCM5B31-09D |  | DF 6-2-3 | 6 | 7 | 261-1-06 | 3/wt |  | TS-PLC-09 | 5-1 | 309-01 | 3/wt | 1:I:9:CH 2 + | 1756-IF16 | Coil 2
74 | Pot Tap 2/1A |  |  |  | IC-3 | 6 | 260-1-06 |  |  | 12 | 260-1-05 |  |  | CR-TS-13 | 13 | 265-1-01 |  | Quench Detector |  | D2HM
| Pot Tap 2/1A |  |  |  | IC-3 | 6 | 260-1-06 |  |  | 12 | 260-1-05 |  |  | CR-TS-13 | 12 | 260-1-01 | bk | SCM5B31-09D |  | DF 6-1-2 | 6 | 6 | 261-1-06 | 2/bk |  | TS-PLC-09 | 3-1 | 309-01 | 2/bk | 1:I:9:CH 1 - | 1756-IF16 | Coil 1
75 | Pot Tap I-L2 |  |  |  | IC-3 | 7 | 260-1-06 |  |  | 13 | 260-1-05 |  |  | CR-TS-13 | 28 | 265-1-01 |  | Quench Detector |  | D4H & D4L
| Pot Tap I-L2 |  |  |  | IC-3 | 7 | 260-1-06 |  |  | 13 | 260-1-05 |  |  | CR-TS-13 | 29 | 260-1-01 | wt | SCM5B31-09D |  | DF 6-5-3 | 6 | 17 | 261-1-06 | 6/wt |  | TS-PLC-09 | 11-1 | 309-01 | 6/wt | 1:I:9:CH 5 + | 1756-IF16 | CL_R
76 | Pot Tap I-L1 |  |  |  | IC-3 | 8 | 260-1-06 |  |  | 14 | 260-1-05 |  |  | CR-TS-13 | 22 | 265-1-01 |  | Quench Detector |  | D2L
| Pot Tap I-L1 |  |  |  | IC-3 | 8 | 260-1-06 |  |  | 14 | 260-1-05 |  |  | CR-TS-13 | 21 | 260-1-01 | bk | SCM5B31-09D |  | DF 6-2-2 | 6 | 9 | 261-1-06 | 3/bk |  | TS-PLC-09 | 6-1 | 309-01 | 3/bk | 1:I:9:CH 2 - | 1756-IF16 | Coil 2
77 | Pot Tap I-M2 |  |  |  | IC-3 | 9 | 260-1-06 |  |  | 15 | 260-1-05 |  |  | CR-TS-12 | 3-1
78 | Pot Tap I-M1 |  |  |  | IC-3 | 10 | 260-1-06 |  |  | 16 | 260-1-05 |  |  | CR-TS-12 | 4-1
79 | Pot Tap I+M1_R |  |  |  | IC-3 | 11 | 260-1-06 |  |  | 17 | 260-1-05 |  |  | CR-TS-12 | 1-2
80 | Pot Tap I+M2_R |  |  |  | IC-3 | 12 | 260-1-06 |  |  | 18 | 260-1-05 |  |  | CR-TS-12 | 2-2
81 | Pot Tap I+L1_R |  |  |  | IC-3 | 13 | 260-1-06 |  |  | 19 | 260-1-05 |  |  | CR-TS-13 | 14
| Pot Tap I+L1_R |  |  |  | IC-3 | 13 | 260-1-06 |  |  | 19 | 260-1-05 |  |  | CR-TS-13 | 15
82 | Pot Tap I+L2_R |  |  |  | IC-3 | 14 | 260-1-06 |  |  | 20 | 260-1-05 |  |  | CR-TS-13 | 7
| Pot Tap I+L2_R |  |  |  | IC-3 | 14 | 260-1-06 |  |  | 20 | 260-1-05 |  |  | CR-TS-13 | 8
83 | Pot Tap 1/1B_R |  |  |  | IC-3 | 15 | 260-1-06 |  |  | 21 | 260-1-05 |  |  | CR-TS-13 | 23
| Pot Tap 1/1B_R |  |  |  | IC-3 | 15 | 260-1-06 |  |  | 21 | 260-1-05 |  |  | CR-TS-13 | 24
84 | Pot Tap 2/1A_R |  |  |  | IC-3 | 16 | 260-1-06 |  |  | 22 | 260-1-05 |  |  | CR-TS-13 | 16
| Pot Tap 2/1A_R |  |  |  | IC-3 | 16 | 260-1-06 |  |  | 22 | 260-1-05 |  |  | CR-TS-13 | 17
85 | Pot Tap I-L2_R |  |  |  | IC-3 | 17 | 260-1-06 |  |  | 23 | 260-1-05 |  |  | CR-TS-13 | 32
| Pot Tap I-L2_R |  |  |  | IC-3 | 17 | 260-1-06 |  |  | 23 | 260-1-05 |  |  | CR-TS-13 | 33
86 | Pot Tap I-L1_R |  |  |  | IC-3 | 18 | 260-1-06 |  |  | 24 | 260-1-05 |  |  | CR-TS-13 | 25
| Pot Tap I-L1_R |  |  |  | IC-3 | 18 | 260-1-06 |  |  | 24 | 260-1-05 |  |  | CR-TS-13 | 26
87 | Pot Tap I-M2_R |  |  |  | IC-3 | 19 | 260-1-06 |  |  | 25 | 260-1-05 |  |  | CR-TS-12 | 3-2
88 | Pot Tap I-M1_R |  |  |  | IC-3 | 20 | 260-1-06 |  |  | 26 | 260-1-05 |  |  | CR-TS-12 | 4-2
| D.C. 1 |  |  |  | IC-3 | 40 | 260-1-06 |  |  | 27 | 260-1-05
| D.C. 2 |  |  |  | IC-3 | 41 | 260-1-06 |  |  | 28 | 260-1-05
| Device | Range | Sensor | Signal | Connector | Connector | Cable | Cable | Wire | Term Strip | Pin | Cable | Cable | Wire | Term Strip | Pin | Cable | Cable | Wire | I/O Channel | I/O Module | PLC
| Liquid Level |  | Name |  |  | Pin# | Label | Type | Color |  | Row-Block | Label | Type | Color |  | Row-block | Label | Type | Color |  |  | Tag Name
89 | LM-500 |  | Helium Sensor | I + | Sensors I/O | 1 |  |  | RD
|  |  | Helium Sensor | I - | Sensors I/O | 2 |  |  | BK
|  |  | Helium Sensor | V+ | Sensors I/O | 3 |  |  | WT
|  |  | Helium Sensor | V - | Sensors I/O | 4 |  |  | GN
|  |  | LN2 Sensor | I + | Sensors I/O | 9 |  |  | RD
|  |  | LN2 Sensor | I - | Sensors I/O | 10 |  |  | BK
|  |  | LN2 Sensor | V+ | Sensors I/O | 11 |  |  | WT
|  |  | LN2 Sensor | V - | Sensors I/O | 12 |  |  | GN
|  |  | Analog Output - | 4-20mA | Sensors I/O | 5 | 250-01 | Alpha 1296C | BL | CR-TS-16 | 1-1 | 250-03 | Alpha 2412C | BK | TS-PLC-08 | 17-1 | 308-01 | Belden 22676 | 8/BK | 8:I.Ch7- | 1756-IF16
|  |  | Analog Output + | 4-20mA | Sensors I/O | 6 | 250-01 | Alpha 1296C | WT | CR-TS-16 | 3-1 | 250-03 | Alpha 2412C | RD | TS-PLC-08 | 16-1 | 308-01 | Belden 22676 | 8/WT | 8:I.Ch7+ | 1756-IF16 | Liquid_Level_meter
|  |  | Sensor Select | 0-5V | Sensors I/O | 7 | 250-01 | Alpha 1296C | OR | CR-TS-16 | 5-1 | 250-05 | Alpha 2412C | RD | TS-PLC-04 | 10-1 | 304-01 | Belden 22676 | 11/WT | 4:O.Ch10+ | 1756-OW16I | He/N2_LL_Select
|  |  | LN2 Control | 0-5V | Sensors I/O | 13 | 250-01 | Alpha 1296C | BK | CR-TS-16 | 2-1 | 250-04 | Alpha 2412C | BK | TS-PLC-01 | 10-1 | 301-01 | Belden 22676 | 6/WT | 1:I.Ch10 | 1756-IV16 | N2_LL_Alarm
|  |  | LHe Control | 0-5V | Sensors I/O | 14 | 250-01 | Alpha 1296C | RD | CR-TS-16 | 4-1 | 250-04 | Alpha 2412C | RD | TS-PLC-01 | 9-1 | 301-01 | Belden 22676 | 5/BK | 1:I.Ch9 | 1756-IV16 | He_LL_Alarm
|  |  | GND | COM | Sensors I/O | 15 | 250-01 | Alpha 1296C | GN | CR-TS-16 | 6-1 | 250-05 | Alpha 2412C | BK | TS-PLC-04 | 10-3 | 304-01 | Belden 22676 | 11/BK | 4:O.Ch10- | 1756-OW16I
[14 empty] | JMPR | TS-PLC-01 | 9-3 |  |  | JMPR | DC-COM
| Line Voltage Controller |  |  | +24VDC | Control Input | 6 | 250-02 | Alpha 3203 | WT | [5 empty] | TS-PLC-04 | 4-1 | 304-01 | Belden 22676 | 5/WT | 4:O.Ch4+ | 1756-OW16I | Power_Liquid_level_meter
|  |  | Channel 1 | COM | Control Input | 1 | 250-02 | Alpha 3203 | RD | [5 empty] | TS-PLC-04 | 4-3 | 304-01 | Alpha 2412C | BK | DC-COM
|  |  | Channel 2 | COM | Control Input | 3 | 250-02 | Alpha 3203 | BK | [5 empty] | TS-PLC-04 | 4-3 | 304-01 | Alpha 2412C | BK | DC-COM
| Device | Range | Sensor | Signal | Connector | Connector | Cable | Cable | Wire | Term Strip | Pin | Cable | Cable | Wire | Connector | Signal | DataForth | Pin | Cable | Cable | Wire | Term Strip | Pin | Cable | Cable | Wire | I/O Module | I/O Module | PLC
| Pressure |  | Name |  |  | Pin # | Label | Type | Color |  | Row-block | Label | Type | Color | Panel/slot/Pin | Conditioner | SCMXIF-DIN | Out | Label | Type | Color |  | Row-block | Label | Type | Color | Channel |  | Tag Name
90 | P_He | 0-100psig | He Pres | V+ | He Pres | A |  |  | GN | CR-TS-16 | 12-1 | 245-03 | Alpha 1896 | WT | DF 4-1-3 | SCM5B38-35D | 4 | 5 | 246-05 | Alpha 6039C | YL | TS-PLC-06 | 10-1 | 306-01 | Belden 22676 | 5/BK | 6:I.Ch9+ | 1756-IF16 | P_He
|  |  |  | V- |  | B |  |  | WT | CR-TS-16 | 13-1 | 245-03 | Alpha 1896 | GN | DF 4-1-2 | SCM5B38-35D | 4 | 6 | 246-05 | Alpha 6039C | BK | TS-PLC-06 | 10-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  |  | I + |  | C |  |  | BK | CR-TS-16 | 11-1 | 245-03 | Alpha 1896 | RD | DF 4-1-4 | SCM5B38-35D
|  |  |  | I - |  | D |  |  | RD | CR-TS-16 | 14-1 | 245-03 | Alpha 1896 | BK | DF 4-1-1 | SCM5B38-35D
91 | P_N2 | 0-100psig | N2 Pres | V+ | N2 Pres | A |  |  | GN | CR-TS-16 | 16-1 | 245-04 | Alpha 1896 | WT | DF 4-2-3 | SCM5B38-35D | 4 | 7 | 246-05 | Alpha 6039C | BN | TS-PLC-06 | 11-1 | 306-01 | Belden 22676 | 6/WT | 6:I.Ch10+ | 1756-IF16 | P_N2
|  |  |  | V- |  | B |  |  | WT | CR-TS-16 | 17-1 | 245-04 | Alpha 1896 | GN | DF 4-2-2 | SCM5B38-35D | 4 | 9 | 246-05 | Alpha 6039C | BK | TS-PLC-06 | 11-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  |  | I + |  | C |  |  | BK | CR-TS-16 | 15-1 | 245-04 | Alpha 1896 | RD | DF 4-2-4 | SCM5B38-35D
|  |  |  | I - |  | D |  |  | RD | CR-TS-16 | 18-1 | 245-04 | Alpha 1896 | BK | DF 4-2-1 | SCM5B38-35D
Vacuum
92 | Vacuum |  | Vacuum Enable + | +24VDC | Vac-D8 | 1 |  | 8-way factory | WT/OR | CR-TS-16 | 7-1 | 245-01 | Alpha 2412C | RD | [7 empty] | TS-PLC-04 | 1-1 | 304-01 | Belden 22676 | 2/WT | 4:O.Ch1+ | 1756-OW16I | Vacuum_power
|  |  | Vacuum Enable - | DC COM | Vac-D8 | 2 |  | 8-way factory | OR | CR-TS-16 | 8-1 | 245-01 | Alpha 2412C | BK | [7 empty] | TS-PLC-04 | 1-3 |  |  | JMPR | DC-COM
|  |  | Vacuum | Signal + | Vac-D8 | 3 |  | 8-way factory | WT/GN | CR-TS-16 | 9-1 | 245-02 | Alpha 2412C | RD | DF 4-0-3 | SCM5B31-03D | 4 | 1 | 246-05 | Alpha 6039C | BL | TS-PLC-06 | 9-1 | 306-01 | Belden 22676 | 5/WT | 6:I.Ch8+ | 1756-IF16 | Vacuum
|  |  |  | ID Resistor | Vac-D8 | 4 |  | 8-way factory
|  |  |  | Signal - | Vac-D8 | 5 |  | 8-way factory | WT/LTBL | CR-TS-16 | 10-1 | 245-02 | Alpha 2412C | BK | DF 4-0-2 | SCM5B31-03D | 4 | 3 | 246-05 | Alpha 6039C | BK | TS-PLC-06 | 9-2 | 306-01 | Belden 22676 | JMPR | RTN
|  |  |  | Set Point | Vac-D8 | 6 |  | 8-way factory
|  |  |  | Calibrate | Vac-D8 | 7 |  | 8-way factory
|  |  |  | N/C | Vac-D8 | 8 |  | 8-way factory
| Device | Range | Sensor | Signal | Connector | Connector | Cable | Cable | Wire | Term Strip | Pin | Cable | Cable | Wire
| JT Motors |  | Name |  |  | Pin# | Label | Type | Color |  | Row-Block | Label | Type | Color | [5 empty] | Cable Label | wire color | Term Strip | Row-block | Cable |  | wire color | Channel | Type | Tag Name
93 | LN2 Bottom | 24 V | MOT_JT1 | C+ | MOT-JT1 | C | 320-01 | Alpha 2414C | WT | CR-TS-15 | 1-1 | 320-07 | Alpha 2414C | WT | Relay Card K1 | ACOM | Close | COIL |  |  |  | TS-PLC-03 | 0-1 | 303-01 |  |  | 1:O:3:CH 0 | 1756-OW16
|  |  | MOT_JT1 | C- | MOT-JT1 | G | 320-01 | Alpha 2414C | RD | CR-TS-15 | 1-2 | 320-07 | Alpha 2414C | RD | Relay Card K1 | BNC |  |  |  | 320-15 | wt | Toggle Switch | A-4
|  |  | MOT_JT1 | O+ | MOT-JT1 | F | 320-01 | Alpha 2414C | GN | CR-TS-15 | 2-1 | 320-07 | Alpha 2414C | GN | Relay Card K2 | ACOM | Open | COIL |  |  |  | TS-PLC-03 | 1-1 | 303-01 |  |  | 1:O:3:CH 1 | 1756-OW16
|  |  | MOT_JT1 | O- | MOT-JT1 | D | 320-01 | Alpha 2414C | BK | CR-TS-15 | 2-2 | 320-07 | Alpha 2414C | BK | Relay Card K2 | BNC |  |  |  | 320-15 | bk | Toggle Switch | B-2
94 | LN2 Top | 24 V | MOT_JT2 | C+ | MOT-JT2 | C | 320-02 | Alpha 2414C | WT | CR-TS-15 | 3-1 | 320-08 | Alpha 2414C | WT | Relay Card K5 | ACOM | Close | COIL |  |  |  | TS-PLC-03 | 2-1 | 303-01 |  |  | 1:O:3:CH 2 | 1756-OW16
|  |  | MOT_JT2 | C- | MOT-JT2 | G | 320-02 | Alpha 2414C | RD | CR-TS-15 | 3-2 | 320-08 | Alpha 2414C | RD | Relay Card K5 | BNC |  |  |  | 320-16 | wt | Toggle Switch | A-4
|  |  | MOT_JT2 | O+ | MOT-JT2 | F | 320-02 | Alpha 2414C | GN | CR-TS-15 | 4-1 | 320-08 | Alpha 2414C | GN | Relay Card K6 | ACOM | Open | COIL |  |  |  | TS-PLC-03 | 3-1 | 303-01 |  |  | 1:O:3:CH 3 | 1756-OW16
|  |  | MOT_JT2 | O- | MOT-JT2 | D | 320-02 | Alpha 2414C | BK | CR-TS-15 | 4-2 | 320-08 | Alpha 2414C | BK | Relay Card K6 | BNC |  |  |  | 320-16 | bk | Toggle Switch | B-2
95 | LHe Cooldown | 24 V | MOT_JT3 | C+ | MOT-JT3 | C | 320-03 | Alpha 2414C | WT | CR-TS-15 | 5-1 | 320-09 | Alpha 2414C | WT | Relay Card K9 | ACOM | Close | COIL |  |  |  | TS-PLC-03 | 4-1 | 303-01 |  |  | 1:O:3:CH 4 | 1756-OW16
|  |  | MOT_JT3 | C- | MOT-JT3 | G | 320-03 | Alpha 2414C | RD | CR-TS-15 | 5-2 | 320-09 | Alpha 2414C | RD | Relay Card K9 | BNC |  |  |  | 320-17 | wt | Toggle Switch | A-4
|  |  | MOT_JT3 | O+ | MOT-JT3 | F | 320-03 | Alpha 2414C | GN | CR-TS-15 | 6-1 | 320-09 | Alpha 2414C | GN | Relay Card K10 | ACOM | Open | COIL |  |  |  | TS-PLC-03 | 5-1 | 303-01 |  |  | 1:O:3:CH 5 | 1756-OW16
|  |  | MOT_JT3 | O- | MOT-JT3 | D | 320-03 | Alpha 2414C | BK | CR-TS-15 | 6-2 | 320-09 | Alpha 2414C | BK | Relay Card K10 | BNC |  |  |  | 320-17 | bk | Toggle Switch | B-2
96 | LHe Bottom Fill | 24 V | MOT_JT4 | C+ | MOT-JT4 | C | 320-04 | Alpha 2414C | WT | CR-TS-15 | 7-1 | 320-10 | Alpha 2414C | WT | Relay Card K13 | ACOM | Close | COIL |  |  |  | TS-PLC-03 | 6-1 | 303-01 |  |  | 1:O:3:CH 6 | 1756-OW16
|  |  | MOT_JT4 | C- | MOT-JT4 | G | 320-04 | Alpha 2414C | RD | CR-TS-15 | 7-2 | 320-10 | Alpha 2414C | RD | Relay Card K13 | BNC |  |  |  | 320-18 | wt | Toggle Switch | A-4
|  |  | MOT_JT4 | O+ | MOT-JT4 | F | 320-04 | Alpha 2414C | GN | CR-TS-15 | 8-1 | 320-10 | Alpha 2414C | GN | Relay Card K14 | ACOM | Open | COIL |  |  |  | TS-PLC-03 | 7-1 | 303-01 |  |  | 1:O:3:CH 7 | 1756-OW16
|  |  | MOT_JT4 | O- | MOT-JT4 | D | 320-04 | Alpha 2414C | BK | CR-TS-15 | 8-2 | 320-10 | Alpha 2414C | BK | Relay Card K14 | BNC |  |  |  | 320-18 | bk | Toggle Switch | B-2
97 | LHe Top Fill | 24 V | MOT_JT5 | C+ | MOT-JT5 | C | 320-05 | Alpha 2414C | WT | CR-TS-15 | 9-1 | 320-11 | Alpha 2414C | WT | Relay Card K17 | ACOM | Close | COIL |  |  |  | TS-PLC-03 | 8-1 | 303-01 |  |  | 1:O:3:CH 8 | 1756-OW16
|  |  | MOT_JT5 | C- | MOT-JT5 | G | 320-05 | Alpha 2414C | RD | CR-TS-15 | 9-2 | 320-11 | Alpha 2414C | RD | Relay Card K17 | BNC |  |  |  | 320-19 | wt | Toggle Switch | A-4
|  |  | MOT_JT5 | O+ | MOT-JT5 | F | 320-05 | Alpha 2414C | GN | CR-TS-15 | 10-1 | 320-11 | Alpha 2414C | GN | Relay Card K18 | ACOM | Open | COIL |  |  |  | TS-PLC-03 | 9-1 | 303-01 |  |  | 1:O:3:CH 9 | 1756-OW16
|  |  | MOT_JT5 | O- | MOT-JT5 | D | 320-05 | Alpha 2414C | BK | CR-TS-15 | 10-2 | 320-11 | Alpha 2414C | BK | Relay Card K18 | BNC |  |  |  | 320-19 | bk | Toggle Switch | B-2
98 | LHe Cold return | 24 V | MOT_JT6 | C+ | MOT-JT6 | C | 320-06 | Alpha 2414C | WT | CR-TS-15 | 11-1 | 320-12 | Alpha 2414C | WT | Relay Card K21 | ACOM | Close | COIL |  |  |  | TS-PLC-03 | 10-1 | 303-01 |  |  | 1:O:3:CH 10 | 1756-OW16
|  |  | MOT_JT6 | C- | MOT-JT6 | G | 320-06 | Alpha 2414C | RD | CR-TS-15 | 11-2 | 320-12 | Alpha 2414C | RD | Relay Card K21 | BNC |  |  |  | 320-20 | wt | Toggle Switch | A-4
|  |  | MOT_JT6 | O+ | MOT-JT6 | F | 320-06 | Alpha 2414C | GN | CR-TS-15 | 12-1 | 320-12 | Alpha 2414C | GN | Relay Card K22 | ACOM | Open | COIL |  |  |  | TS-PLC-03 | 11-1 | 303-01 |  |  | 1:O:3:CH 11 | 1756-OW16
|  |  | MOT_JT6 | O- | MOT-JT6 | D | 320-06 | Alpha 2414C | BK | CR-TS-15 | 12-2 | 320-12 | Alpha 2414C | BK | Relay Card K22 | BNC |  |  |  | 320-20 | bk | Toggle Switch | B-2
99 | He Warm Return | 24 V | MOT_BV7 | C+ | MOT-BV7 | 1 | 320-13 | Alpha 2414C | WT | CR-TS-15 | 13-1 | 320-14 | Alpha 2414C | WT | Relay Card Ch23 | ACOM | Close | COIL |  |  |  | TS-PLC-03 | 12-1 | 303-01 |  |  | 1:O:3:CH 12 | 1756-OW16
|  |  | MOT_BV7 | C- | MOT-BV7 | 2 | 320-13 | Alpha 2414C | RD | CR-TS-15 | 13-2 | 320-14 | Alpha 2414C | RD | Relay Card Ch23 | BNC |  |  |  | 320-21 | wt | Toggle Switch | A-4
|  |  | MOT_BV7 | O+ | MOT-BV7 | 3 | 320-13 | Alpha 2414C | GN | CR-TS-15 | 14-1 | 320-14 | Alpha 2414C | GN | Relay Card Ch24 | ACOM | Open | COIL |  |  |  | TS-PLC-03 | 13-1 | 303-01 |  |  | 1:O:3:CH 13 | 1756-OW16
|  |  | MOT_BV7 | O- | MOT-BV7 | 4 | 320-13 | Alpha 2414C | BK | CR-TS-15 | 14-2 | 320-14 | Alpha 2414C | BK | Relay Card Ch24 | BNC |  |  |  | 320-32 | bk | Toggle Switch | B-2
100 | Key Switch | 24 V | Local /remote |  |  | A1 |  | Curcuit Beaker | Valve-1
A2
B3
B4
C5
C6
| LVDT | Range | Sensor | Signal | Connector | Connector | Cable | Cable | Wire | Term Strip | Pin | Cable | Cable | Wire | Macro Sensor |  | Cable Type | wire color |  | Term Strip | Pin | PLC | wire color | I/O Module |  | I/O Module | PLC
|  |  | Name |  |  | Pin # | Label | Type | Color |  | Row-block | Label |  | Color | Input side | Output Side | Cable Label |  |  |  | Row-block | Cable |  | Channel |  | Type | Tag Name
101 | LN2 Bottom | 4-20 mA | LVDT-1 |  | LVDT-1 | A | 280-05 |  |  | CR-TS-14 | 1 | 280-01 |  | RD | 7 | 9 | 282-01 | rd |  | 8-Position-Selector | 1
[6 empty] | D | 280-05 |  |  | CR-TS-14 | 2 | 280-01 |  | WT | 8 | 12 | 280-09 | wt |  | TS-PLC-08 | 0-1 | 308-01 | 1/wt | 5:I:8: Ch 0 + |  | 1756-IF16 | JT1
[6 empty] | E | 280-05 |  |  | CR-TS-14 | 3 | 280-01 |  | GN | 3 | 11 | 280-09 | bk |  | TS-PLC-08 | 1-1 | 308-01 | 1/bk | 5:I:8: Ch 0 -
[6 empty] | F | 280-05 |  |  | CR-TS-14 | 4 | 280-01 |  | BK | 4
102 | LN2 Top | 4-20 mA | LVDT-2 |  | LVDT-2 | A | 280-06 |  |  | CR-TS-14 | 6 | 280-02 |  | RD | 7 | 9 | 282-01 | wt |  | 8-Position-Selector | 2
[6 empty] | D | 280-06 |  |  | CR-TS-14 | 7 | 280-02 |  | WT | 8 | 12 | 280-10 | wt |  | TS-PLC-08 | 2-1 | 308-01 | 2/wt | 5:I:8: Ch 1 + |  | 1756-IF16 | JT2
[6 empty] | E | 280-06 |  |  | CR-TS-14 | 8 | 280-02 |  | GN | 3 | 11 | 280-10 | bk |  | TS-PLC-08 | 3-1 | 308-01 | 2/bk | 5:I:8: Ch 1 -
[6 empty] | F | 280-06 |  |  | CR-TS-14 | 9 | 280-02 |  | BK | 4
103 | LHe Cooldown | 4-20 mA | LVDT-3 |  | LVDT-3 | A | 280-07 |  |  | CR-TS-14 | 11 | 280-03 |  | RD | 7 | 9 | 282-01 | bk |  | 8-Position-Selector | 3
[6 empty] | D | 280-07 |  |  | CR-TS-14 | 12 | 280-03 |  | WT | 8 | 12 | 280-11 | wt |  | TS-PLC-08 | 2-1 | 308-01 | 3/wt | 5:I:8: Ch 2 + |  | 1756-IF16 | JT3
[6 empty] | E | 280-07 |  |  | CR-TS-14 | 13 | 280-03 |  | GN | 3 | 11 | 280-11 | bk |  | TS-PLC-08 | 3-1 | 308-01 | 3/bk | 5:I:8: Ch 2 -
[6 empty] | F | 280-07 |  |  | CR-TS-14 | 14 | 280-03 |  | BK | 4
104 | LHe Bottom Fill | 4-20 mA | LVDT-4 |  | LVDT-4 | A | 280-08 |  |  | CR-TS-14 | 16 | 280-04 |  | RD | 7 | 9 | 282-01 | bl |  | 8-Position-Selector | 4
[6 empty] | D | 280-08 |  |  | CR-TS-14 | 17 | 280-04 |  | WT | 8 | 12 | 280-12 | wt |  | TS-PLC-08 | 2-1 | 308-01 | 4/wt | 5:I:8: Ch 3 + |  | 1756-IF16 | JT4
[6 empty] | E | 280-08 |  |  | CR-TS-14 | 18 | 280-04 |  | GN | 3 | 11 | 280-12 | bk |  | TS-PLC-08 | 3-1 | 308-01 | 4/bk | 5:I:8: Ch 3 -
[6 empty] | F | 280-08 |  |  | CR-TS-14 | 19 | 280-04 |  | BK | 4
105 | LHe Top Fill | 4-20 mA | LVDT-5 |  | LVDT-5 | A | 281-03 |  |  | CR-TS-14 | 21 | 281-01 |  | RD | 7 | 9 | 282-01 | gn |  | 8-Position-Selector | 5
[6 empty] | D | 281-03 |  |  | CR-TS-14 | 22 | 281-01 |  | WT | 8 | 12 | 281-05 | wt |  | TS-PLC-08 | 2-1 | 308-01 | 5/wt | 5:I:8: Ch 4 + |  | 1756-IF16 | JT5
[6 empty] | E | 281-03 |  |  | CR-TS-14 | 23 | 281-01 |  | GN | 3 | 11 | 281-05 | bk |  | TS-PLC-08 | 3-1 | 308-01 | 5/bk | 5:I:8: Ch 4 -
[6 empty] | F | 281-03 |  |  | CR-TS-14 | 24 | 281-01 |  | BK | 4
106 | LHe Cold Return | 4-20 mA | LVDT-6 |  | LVDT-6 | A | 281-04 |  |  | CR-TS-14 | 26 | 281-02 |  | RD | 7 | 9 | 282-01 | bn |  | 8-Position-Selector | 6
[6 empty] | D | 281-04 |  |  | CR-TS-14 | 27 | 281-02 |  | WT | 8 | 12 | 281-06 | wt |  | TS-PLC-08 | 2-1 | 308-01 | 6/wt | 5:I:8: Ch 5 + |  | 1756-IF16 | JT6
[6 empty] | E | 281-04 |  |  | CR-TS-14 | 28 | 281-02 |  | GN | 3 | 11 | 281-06 | bk |  | TS-PLC-08 | 3-1 | 308-01 | 6/bk | 5:I:8: Ch 5 -
[6 empty] | F | 281-04 |  |  | CR-TS-14 | 29 | 281-02 |  | BK | 4
107 | He Warm return | 4-20 mA | Warm return |  |  | +
-
108 | Valve Position meter | 8-POS | Selector Switch |  |  | 1 | 282-01 |  | rd | LVDT 1 | 9
[6 empty] | 2 | 282-01 |  | wt | LVDT 2 | 9
[6 empty] | 3 | 282-01 |  | bk | LVDT 3 | 9
[6 empty] | 4 | 282-01 |  | bl | LVDT 4 | 9
[6 empty] | 5 | 282-01 |  | gn | LVDT 5 | 9
[6 empty] | 6 | 282-01 |  | br | LVDT 6 | 9
[6 empty] | 7 |  |  |  | No Connection
[6 empty] | 8 |  |  |  | No Connection
[6 empty] | COMM |  |  | yl | Red Lion | INP+
|  | 0-5V | Red Lion |  |  | INP + |  |  |  | Selector Switch | COMM
[6 empty] | COMM |  |  |  | Macro Sensor | 15
[6 empty] | USR |  |  |  | No Connection
[6 empty] | USR Comm |  |  |  | No Connection
[6 empty] | Pwr Comm |  |  |  | 24 V PSU GND
[6 empty] | 9-28 VDC |  |  |  | 24 V PSU
| MPS |  | Connector | Signal | Type | Pin # |  | Signal | Wire color | Term Strip | Pin # | Cable # | Color | Cable
109 | Course Current signal | 0-3 V | BNC | V+ |  | Co-axial | MPS-Current | Co-axial | center | CR-TS-16 | 23-1 | 245-08 | sw | DF 4-5-3 | SCM5B31-03D | 4 | 17 | 245-07 |  | 6/wt | TS-PLC-06 | 15-1 | 306-01 |  |  | 1:I:6:CH 13 + | 1756-IF16 | MPS_Current
|  |  | BNC | V - |  | C0-axial | MPS_Current | Co-axial | shield | CR-TS-16 | 24-1 | 245-08 | rt | DF 4-5-2 |  | 4 | 18 | 245-07 |  | 6/bk | TS-PLC-06 | 15-2 | 306-01 |  |  | 1:I:6:CH 13 - | 1756-IF16
|  |  | Connector | Signal |  | Pin # |  | Connector | Pin # | Cable # | Color | Term Strip | Pin # | Cable | Term Strip | Pin | Cable | wire color |  | I/O Channel | I/O Module
| Status Board |  | Plug 12 | 480 on |  | 5 | Status Signal | Plug 1 | 1 | 290-01 | bk | CR-TS-17 | 1-1 | 290-2 | TS-PLC-06 | 12-1 | 301-01 | 8w |  | 1:I:6:CH 12 + | 1756-IV16
|  |  | Plug 12 | Main Pwr |  | 3 | Status Signal | Plug 1 | 2 | 290-01 | wt | CR-TS-17 | 2-1 | 290-2 | TS-PLC-06 | 13-1 | 301-01 | 9b |  | 1:I:6:CH 13 + | 1756-IV16
|  |  | Plug 12 | Ready |  | 2 | Status Signal | Plug 1 | 3 | 290-01 | rd | CR-TS-17 | 3-1 | 290-2 | TS-PLC-06 | 14-1 | 301-01 | 9w |  | 1:I:6:CH 14 + | 1756-IV16
|  |  | Plug 12 | Sum Intl |  | 4 | Status Signal | Plug 1 | 4 | 290-01 | gr | CR-TS-17 | 4-1 | 290-2 | TS-PLC-06 | 15-1 | 301-01 | 10b |  | 1:I:6:CH 15 + | 1756-IV16
|  |  | Plug 12 | Gnd |  | 6 | Status Signal | Plug 1 | 5 | 290-01 | br | CR-TS-17 | 5-1 | 290-2 | TS-PLC-06 | 16-3 | 24 V DC gnd | All 3rd rows jmper to gnd
110 | Mass Flow LCL | 4-20 mA |  | 4-20 mA | 8 pin Mini Din | 1 | MF-LCL |  | bk | CR-TS-18 | 1-1 | 245-09 |  |  | DF 4-3-3 | SCM5B31-03D | 4 | 11 |  | 245-07 | 4/wt | TS-PLC-06 | 12-1 | 306-01 |  |  | 1:I:6:CH 11 + | 1756-IF16 | Mass Flow LCL
|  |  |  | Ground | 8 pin Mini Din | 8 | MF-LCL |  | br | CR-TS-18 | 1-2 | 245-09 |  |  | DF 4-3-2 |  | 4 | 12 |  | 245-07 | 4/bk | TS-PLC-06 | 12-2 | 306-01 |  |  | 1:I:6:CH 11 - | 1756-IF16
|  |  |  | Input V+ | 8 pin Mini Din | 4 | MF-LCL |  | rd | CR-TS-18 | 2-1
|  |  |  | Power | 8 pin Mini Din | 7 | MF-LCL |  | or | CR-TS-18 | 2-2
|  |  |  | 0-10VDC Out | 8 pin Mini Din | 6 | MF-LCL |  | ye
|  |  |  | RS-232 In | 8 pin Mini Din | 3 | MF-LCL |  | grn
|  |  |  | RS-232 Out | 8 pin Mini Din | 5 | MF-LCL |  | bl
|  |  |  | Alarm | 8 pin Mini Din | 2 | MF-LCL |  | pu
111 | Mass Flow RCL | 4-20 mA |  | 4-20 mA | 8 pin Mini Din | 1 | MF-RCL |  | bk | CR-TS-18 | 3-1 | 245-09 |  |  | DF 4-4-3 | SCM5B31-03D | 4 | 13 |  | 245-07 | 5/wt | TS-PLC-06 | 13-1 | 306-01 |  |  | 1:I:6:CH 12 + | 1756-IF16 | Mass Flow RCL
|  |  |  | Ground | 8 pin Mini Din | 8 | MF-RCL |  | br | CR-TS-18 | 3-2 | 245-09 |  |  | DF 4-4-2 |  | 4 | 17 |  | 245-07 | 5/bk | TS-PLC-06 | 13-2 | 306-01 |  |  | 1:I:6:CH 12 - | 1756-IF16
|  |  |  | Input V+ | 8 pin Mini Din | 4 | MF-RCL |  | rd | CR-TS-18 | 4-1
|  |  |  | Power | 8 pin Mini Din | 7 | MF-RCL |  | or | CR-TS-18 | 4-2
|  |  |  | 0-10VDC Out | 8 pin Mini Din | 6 | MF-RCL |  | ye
|  |  |  | RS-232 In | 8 pin Mini Din | 3 | MF-RCL |  | grn
|  |  |  | RS-232 Out | 8 pin Mini Din | 5 | MF-RCL |  | bl
|  |  |  | Alarm | 8 pin Mini Din | 2 | MF-RCL |  | pu
| Constant Current Source |  |  |  | Plug | Pin | Cable |  | Wire | Device | Pin |  | Term Strip | Pin | PLC | wire color | I/O Module | I/O Module
|  | Board |  |  |  |  | Label |  | Color |  |  |  |  | Row-block | Cable |  | Channel | Type
112 | Carbon Glass | A |  |  | PL01 | + 30 VDC | 310-06 |  | JMPER | A +15 VDC | +24V
| Carbon Glass | A |  |  | PL01 | COM | 310-06 |  | BK | 24V DC PSU | GND
| Carbon Glass | A |  |  | PL01 | + 15 VDC | 310-06 |  | WT | 24V DC PSU | +24V
| Carbon Glass | A |  |  | J1 | CH 1+ | 235-01 |  | rd | CG-1
| Carbon Glass | A |  |  | J1 | CH 1- | 235-01 |  | bk | CG-1
| Carbon Glass | A |  |  | J1 | CH 2+ | 235-02 |  | rd | CG-2
| Carbon Glass | A |  |  | J1 | CH 2- | 235-02 |  | bk | CG-2
| Carbon Glass | A |  |  | J1 | CH 3+ | 235-03 |  | rd | CG-3
| Carbon Glass | A |  |  | J1 | CH 3- | 235-03 |  | bk | CG-3
| Carbon Glass | A |  |  | J1 | CH 4+ | 235-04 |  | rd | CG-4
| Carbon Glass | A |  |  | J1 | CH 4- | 235-04 |  | bk | CG-4
| Carbon Glass | A |  |  | J1 | CH 5+ | 236-01 |  | rd | CG-5
| Carbon Glass | A |  |  | J1 | CH 5- | 236-01 |  | bk | CG-5
| Carbon Glass | A |  |  | J1 | CH 6+ | 236-02 |  | rd | CG-6
| Carbon Glass | A |  |  | J1 | CH 6- | 236-02 |  | bk | CG-6
| Carbon Glass | A |  |  | J1 | CH 7+ | 236-03 |  | rd | CG-7
| Carbon Glass | A |  |  | J1 | CH 7- | 236-03 |  | bk | CG-7
| Carbon Glass | A |  |  | J1 | CH 8+
| Carbon Glass | A |  |  | J1 | CH 8-
| Carbon Glass | A |  |  | J2 | CH 1+ | 295-01 |  | WT |  |  |  | TS-PLC-04 | 0-1 | 304-01 | 1/wt | 1:I:4:CH 0 + | 1756-OW16I |  | He-CG Current enabled
| Carbon Glass | A |  |  | J2 | CH 1- | 295-01 |  | BK |  |  |  | TS-PLC-04 | 0-3 | 304-01 | 1/bk | 1:I:4:CH 0 - | 1756-OW16I
| Carbon Glass | A |  |  | J2 | CH 2+ | J2-CH 1+ |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 2- | J2-CH 1- |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 3+ | J2-CH 2+ |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 3- | J2-CH 2- |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 4+ | J2-CH 3+ |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 4- | J2-CH 3- |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 5+ | J2-CH 4+ |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 5- | J2-CH 4- |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 6+ | J2-CH 5+ |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 6- | J2-CH 5- |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 7+ | J2-CH 6+ |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 7- | J2-CH 6- |  | JMPER
| Carbon Glass | A |  |  | J2 | CH 8+
| Carbon Glass | A |  |  | J2 | CH 8-
113 | Diode | B |  |  | PL01 | + 30 VDC | 310-06 |  | JMPER | B +15 VDC | +24V
| Diode | B |  |  | PL01 | COM | 310-06 |  | BK | 24V DC PSU | GND
| Diode | B |  |  | PL01 | + 15 VDC | 310-06 |  | WT | 24V DC PSU | +24V
| Diode | B |  |  | J1 | CH 1+ | 238-01 |  | rd | Diode 1
| Diode | B |  |  | J1 | CH 1- | 238-01 |  | bk | Diode 1
| Diode | B |  |  | J1 | CH 2+ | 238-02 |  | rd | Diode 2
| Diode | B |  |  | J1 | CH 2- | 238-02 |  | bk | Diode 2
| Diode | B |  |  | J1 | CH 3+ | 238-03 |  | rd | Diode 3
| Diode | B |  |  | J1 | CH 3- | 238-03 |  | bk | Diode 3
| Diode | B |  |  | J1 | CH 4+ | 238-04 |  | rd | Diode 4
| Diode | B |  |  | J1 | CH 4- | 238-04 |  | bk | Diode 4
| Diode | B |  |  | J1 | CH 5+
| Diode | B |  |  | J1 | CH 5-
| Diode | B |  |  | J1 | CH 6+
| Diode | B |  |  | J1 | CH 6-
| Diode | B |  |  | J1 | CH 7+
| Diode | B |  |  | J1 | CH 7-
| Diode | B |  |  | J1 | CH 8+
| Diode | B |  |  | J1 | CH 8-
| Diode | B |  |  | J2 | CH 1+ | 296-01 |  | WT |  |  |  | TS-PLC-04 | 11-1 | 304-01 | 12/wt | 1:I:4:CH 11 + | 1756-OW16I |  | Diode Current Enabled
| Diode | B |  |  | J2 | CH 1- | 296-01 |  | BK |  |  |  | TS-PLC-04 | 11-3 | 304-01 | 12/bk | 1:I:4:CH 11 - | 1756-OW16I
| Diode | B |  |  | J2 | CH 2+ | J2-CH 1+ |  | JMPER
| Diode | B |  |  | J2 | CH 2- | J2-CH 1- |  | JMPER
| Diode | B |  |  | J2 | CH 3+ | J2-CH 2+ |  | JMPER
| Diode | B |  |  | J2 | CH 3- | J2-CH 2- |  | JMPER
| Diode | B |  |  | J2 | CH 4+ | J2-CH 3+ |  | JMPER
| Diode | B |  |  | J2 | CH 4- | J2-CH 3- |  | JMPER
| Diode | B |  |  | J2 | CH 5+
| Diode | B |  |  | J2 | CH 5-
| Diode | B |  |  | J2 | CH 6+
| Diode | B |  |  | J2 | CH 6-
| Diode | B |  |  | J2 | CH 7+
| Diode | B |  |  | J2 | CH 7-
| Diode | B |  |  | J2 | CH 8+
| Diode | B |  |  | J2 | CH 8-
114 | Quench Dectector | Pin # | input | cable # | wire color | terminal | Pin #
| Plug 1 | 1 | D1H | 265-02 | bk | CR-TS-19 | 1-1
| Plug 1 | 2 | D1HM | 265-02 | wt | CR-TS-19 | 1-2
| Plug 1 | 3 | D1LM | 265-02 | rd | CR-TS-19 | 2-1
| Plug 1 | 4 | D1LM | 265-02 | gr | CR-TS-19 | 2-2
| Plug 2 | 1 | D2H | 265-02 | br | CR-TS-19 | 3-1
| Plug 2 | 2 | D2HM | 265-02 | bl | CR-TS-19 | 3-2
| Plug 2 | 3 | D2LM | 265-02 | or | CR-TS-19 | 4-1
| Plug 2 | 4 | D2LM | 265-02 | ye | CR-TS-19 | 4-2
| Plug 3 | 1 | D3H | 265-03 | bk | CR-TS-19 | 5-1
| Plug 3 | 2 | D3HM | 265-03 | wt | CR-TS-19 | 5-2
| Plug 3 | 3 | D3LM | 265-03 | rd | CR-TS-19 | 6-1
| Plug 3 | 4 | D3LM | 265-03 | gr | CR-TS-19 | 6-2
| Plug 4 | 1 | D4H | 265-03 | br | CR-TS-19 | 7-1
| Plug 4 | 2 | D4HM | 265-03 | bl | CR-TS-19 | 7-2
| Plug 4 | 3 | D4LM | 265-03 | or | CR-TS-19 | 8-1
| Plug 4 | 4 | D4LM | 265-03 | ye | CR-TS-19 | 8-2
| Plug 5 | 1 | U1 | 265-05 | bk | CR-TS-19 | 9-1
| Plug 5 | 2 | L1 | 265-05 | wt | CR-TS-19 | 9-2
| Plug 5 | 3 | U2 | 265-05 | rd | CR-TS-19 | 10-1
| Plug 5 | 4 | L2 | 265-05 | gr | CR-TS-19 | 10-2
| Plug 5 | 5 | U3 | 265-05 | br | CR-TS-19 | 11-1
| Plug 5 | 6 | L3 | 265-05 | bl | CR-TS-19 | 11-2
| Plug 5 | 7 | U4 | 265-05 | or | CR-TS-19 | 12-1
| Plug 5 | 8 | L4 | 265-05 | ye | CR-TS-19 | 12-2
| Plug 5 | 9 | SUM | 265-05 | vi | CR-TS-19 | 13-1
| Plug 5 | 10 | +30V | 265-05 | gy | CR-TS-19 | 14-1
| Plug 5 | 11 | GND | 265-05 | pk | CR-TS-19 | 15-1
| Plug 5 | 12 | Quench NO | 265-08 | bk | CR-TS-19 | 16-1
| Plug 5 | 13 | Quench Common | 265-08 | wh | CR-TS-19 | 17-1
| Plug 5 | 14 | Quench NC | 265-08 | rd | CR-TS-19 | 18-1
| Plug 6 | 1 | reset | 265-06 | rd | CR-TS-19 | 19-1
| Plug 6 | 2 | common | 265-06 | bk | CR-TS-19 | 19-2
| Plug 7 | 1 | 24 VAC | 265-10 | rd | 265-11 | 20-1 | 25 Vac Transformer
| Plug 7 | 2 | GND
| Plug 7 | 3 | 24 VAC | 265-10 | bk | 265-11 | 20-2
115 | RS232 |  | Connector | Signal | Type | Pin # |  | Signal | Wire color | Unit | Type | Pin # | Unit | Cable
|  |  | MPS-Plug14 | TX/RX | DB25 | 2 |  | 2400 Baud | RD | MVI 94 | DB9 | 2 | Flex I/O | RG6 | Control Net Tap
|  |  | MPS-Plug14 | RX/TX | DB25 | 3 |  | 8 data | WT | MVI 94 | DB9 | 3
|  |  | MPS-Plug14 | GND | DB25 | 7 |  | 1 stop | BK | MVI 94 | DB9 | 5
[8 empty] | No Parity |  | 24V
[8 empty] | No Protocol |  | 24 V GND
Relays
| Signal |  | Pin # |  |  |  | Cable # | Color | Term Strip | Pin # | Cable # | Color | Term Strip | Pin | Cable | wire color | I/O Channel | I/O Module
| Fast Disharge |  | 6 |  |  |  | 290-01 | bl | CR-TS-16 | 30-1 | 290-01 | bl | TS-PLC-06 | 7-1 | 290-03
|  |  | 5 |  |  |  | 290-01 | or | CR-TS-16 | 30-2 | 290-01 | or | TS-PLC-06 |  | 290-03
|  |  | 3 |  |  |  | 290-01 | ye | CR-TS-16 | 31-1 | 290-01 | ye | TS-PLC-06 |  | 290-03
|  |  | 4 |  |  |  | 290-01 | vi | CR-TS-16 | 31-2 | 290-01 | vi | TS-PLC-06 |  | 290-03
| Keep Alive Relay |  | 29804TR
| timed relay |  | 1 | Common 1 |  | TS-PLC-04 | 3-1 | 1:O:4:CH 3 +
| B010S |  | 2 | 24 V |  | TS-PLC-04 | 16-2 | 24 V
|  |  | 3 | NO 1 |  | 29808 CR | 2
|  |  | 4 | NC 1 |  | TS-PLC-04
|  |  | 5 | return |  | TS-PLC-04 | 4-1 | 1:O:4:CH 4 +
|  |  | 6 | control |  | TS-PLC-04 | 4-2 | 1:O:4:CH 4 -
|  |  | 7 | Not used |  | TS-PLC-04
|  |  | 8 | Common 2
|  |  | 9 | NO 2
|  |  | 10 | 24 V Gnd |  | TS-PLC-04 | 16-3 | 24 V GND
|  |  | 11 | NC 2
29808CR
|  |  | 1 | Common 1 | fast discharge | TS-PLC-04 | 5-1 | 1:O:4:CH 5 +
|  |  | 2 | 24 V |  | 29804TR | 3
|  |  | 3 | NO 1 |  | CR-TS-17 | 17-1 | QD
|  |  | 4 | NC 1
|  |  | 5 | NC 2
|  |  | 6 | Common 2 | Slow disharge | TS-PLC-04 | 6-1 | 1:O:4:CH 6 +
|  |  | 7 | NO 2 |  | CR-TS-16 | 31-1 | MPS | pin 3
|  |  | 8 | Common 3 | 24 V
|  |  | 9 | NC 3 |  | 29804TR | 1 | QD
|  |  | 10 | 24 V Gnd |  | 29804TR | 10 | 24 V GND
|  |  | 11 | NC 3 |  | 29804TR | 2 | 24V
| MPS_CPU reset |  |  | MPS | TP-4 | CR-TS-16 | 33-1
|  |  |  | MPS | TP-6 | CR-TS-16 | 33-2
| MPS Diodes reset |  |  | MPS |  | CR-TS-16 | 32-1
|  |  |  | MPS |  | CR-TS-16 | 32-2
Diode CCS enabled
CG CCS enabled
Liquid Level Pwr
Liquid Level Select
Interlocks
| QD-U1 |  |  |  | LiYCY 4 * .14 | MPS_DIS |  |  | ws |  | 00
[5 empty] | LiYCY 4 * .14 | MPS_DIS |  |  | br
QD-L1
[5 empty] | LiYCY 4 * .14 | MPS_DIS |  |  | gn
| QD-U2 |  |  |  | LiYCY 4 * .14 | MPS_DIS |  |  | ge | [17 empty] | Dipole:4:O.Ch12Data | 1756-OW16I | 1756-OW16I
QD-L2
[27 empty] | Dipole:4:O.Ch11Data | 1756-OW16I | 1756-OW16I
QD-U3
QD-L3
QD-U4
QD-L4
QD-SUM
He-LL alarm
| 24 Volt PSU |  |  |  | Amps
|  | + 24 V | CB-1 (10A) | CB-2 | 2 |  | TS-PLC-01
|  |  |  | CB-3 | 2 |  | TS-PLC-02
|  |  |  | CB-4 | 2 |  | TS-PLC-04
|  |  |  | CB-5 | 2 |  | TS-PLC-06
|  |  |  | CB-6 | 2
|  |  |  | CB-7 | 2 |  | Constant Current Source
|  |  |  | CB-8 | 5 |  | LVDT macro sensor
|  | GND | CR-TS-25 | 1-1 |  |  | TS-PLC-01
|  |  | CR-TS-25 | 2-1 |  |  | TS-PLC-02
|  |  | CR-TS-25 | 3-1 |  |  | TS-PLC-04
|  |  | CR-TS-25 | 4-1 |  |  | TS-PLC-06
|  |  | CR-TS-25 | 5-1
|  |  | CR-TS-25 | 6-1 |  |  | Constant Current Source
|  |  | CR-TS-25 | 7-1 |  |  | LVDT macro sensor
|  |  | CR-TS-25 | 8-1
| 24 Volt PSU |  | JT Motors |  | Amps
|  | + 24 V | CB-21 (10A) | CB-22 | 2 |  | Key switch
|  |  |  | CB-23 | 2 |  | Drive Motors
|  |  |  | CB-24 | 2 |  | Drive Motors
|  |  |  | CB-25 | 2 |  | Drive Motors
|  | GND | CR-TS-26 | 1-1 |  |  | Key switch
|  |  | CR-TS-26 | 2-1 |  |  | Drive Motors
|  |  | CR-TS-26 | 3-1 |  |  | Drive Motors
|  |  | CR-TS-26 | 4-1 |  |  | Drive Motors
5 Volt PSU
|  | + 5V | CB-10 | CB-10 | 2 |  | DF Board | 1 | TB 9 | +5
|  |  |  | CB-11 | 2 |  | DF Board | 2 | TB 9 | +5
|  |  |  | CB-12 | 2 |  | DF Board | 3 | TB 9 | +5
|  |  |  | CB-13 | 2 |  | DF Board | 4 | TB 9 | +5
|  |  |  | CB-14 | 2 |  | DF Board | 5 | TB 9 | +5
|  |  |  | CB-15 | 2 |  | DF Board | 6 | TB 9 | +5
|  | GND | CR-TS-25 | 1-2 |  |  | DF Board | 1 | TB 9 | PCOM
|  |  | CR-TS-25 | 2-2 |  |  | DF Board | 2 | TB 9 | PCOM
|  |  | CR-TS-25 | 3-2 |  |  | DF Board | 3 | TB 9 | PCOM
|  |  | CR-TS-25 | 4-2 |  |  | DF Board | 4 | TB 9 | PCOM
|  |  | CR-TS-25 | 5-2 |  |  | DF Board | 5 | TB 9 | PCOM
|  |  | CR-TS-25 | 6-2 |  |  | DF Board | 6 | TB 9 | PCOM

## Cable 4 Components
In Hall Cable |  | Qty | [5 empty] | In House
Component | Wire/cable | HB | Q1 | Q2 | Q3 | Dipole | HX
He Liquid Level | 9 | 1 | 1 | 1 | 1 | 1 |  | X
N2 Liquid Level | 9 | 1 | 1 | 1 | 1 | 1 |  | X
Pressure He | 4 | 1 | 1 | 1 | 1 | 1 | 1
Pressure N2 | 4 | 1 | 1 | 1 | 1 | 1 | 1
Vaccum (cat 5) | 8 | 1 | 1 | 1 | 1 | 1 | 1
He Mass Flow Controllers (Mini Din) | 8 | 2 | 2 | 2 | 2 | 2
Current Lead Heaters | 4 | 1 | 1 | 1 | 1 | 1
JT Motors | 4 | 6 | 6 | 6 | 6 | 6 | 2
JT LVDT | 4 | 6 | 6 | 6 | 6 | 6 | 2
Warm Return Valve | 8 | 1 | 1 | 1 | 1 | 1
A | 30 | 1 | 1 | 1 | 1 | 1 | 1
B | 30 | 1 | 1 | 1 | 1 | 1
C | 30 | 1 | 1 | 1 | 1 | 1
1 | 50 | 1 | 1 | 1 | 1 | 1
2 | 50 | 1 | 1 | 1 | 1 | 1
3 | 30 | 1 | 1 | 0 | 0 | 0
4 | 50 | 0 | 0 | 1 | 1 | 1
Strain gages | 8 | 10 | 8 | 8 | 8 | 8
Hall Probes (C050G) | 8 | 1 | 1 | 1 | 1 | 0
NMR | Coaxial | 0 | 0 | 0 | 0 | 5
Length from device to Control Rack (ft) |  | 90 | 86 | 77 | 68 | 61 | 90
using lengths of LL probes
[8 empty] | Total ft | Add 10% | 500 ft reels | Unit Cost/500 ft | Cost
5464C 20AWG | 4 | 1260 | 1204 | 1078 | 952 | 854 | 630 | 5978 | 6575.8 | 14 | 1663 | 23282
5468C 20AWG | 8 | 1080 | 860 | 770 | 680 | 549 |  | 3939 | 4332.9 | 9 | 2451 | 22059
OLFLEX 601841-SHLD 18AWG | 41 | 540 | 516 | 385 | 340 | 305 |  | 2086 | 2294.6 | 5 | Not available
5470/30C | 30 | 360 | 344 | 231 | 204 | 183 | 90 | 1412 | 1553.2 | 4 | 9522 | 38088
5470/50C | 50 | 180 | 172 | 231 | 204 | 183 |  | 970 | 1067 | 3 | 17298 | 51894
1624R 24AWG 4 pr | Cat5 | 90 | 86 | 77 | 68 | 61 |  | 382 | 420.2 | 1 | 494 | 494
MiniDin 24 AWG | MiniDin | 180 | 172 | 154 | 136 | 122 |  | 764 | 840.4 | 2 | 494 | 988
Coaxial | Coaxial | 0 | 0 | 0 | 0 | 305 |  | 305 | 335.5 | 1 | 88 | 88
136893