DGH Windows Device Driver for LABTECH Notebook and Control Software Products

Document Version 1.00 (4/6/95)

Warranty:

This DGH documentation and the software described in it are copyrighted with all rights reserved. Under the copyright laws, neither the documentation nor the software may be copied, photocopied, reproduced, translated, or reduced to any electronic medium or machine readable form, in whole or in part, without the prior written consent of DGH Corporation.

DGH Corporation does not warrant that the D1000, D2000, D3000 and D4000 series device driver software will function properly in every hardware/software environment. The device driver may not work in combination with modified versions of the operating system, with other programs using the real-time clock of the computer, or with certain file facility programs. This software is inherently complex, and users are cautioned to verify the results of their work.

Although DGH Corporation has tested the software and reviewed the supplied documentation, DGH CORPORATION MAKES NO WARRANTY OR REPRESENTATION, EITHER EXPRESS OR IMPLIED, WITH RESPECT TO THIS SOFTWARE OR DOCUMENTATION, THEIR QUALITY, PERFORMANCE, MERCHANTABILITY, OR FITNESS FOR A PARTICULAR PURPOSE. AS A RESULT, THIS SOFTWARE AND DOCUMENTATION ARE LICENSED "AS IS", AND YOU, THE LICENSEE, ARE ASSUMING THE ENTIRE RISK AS TO THEIR QUALITY AND PERFORMANCE.

IN NO EVENT WILL DGH CORPORATION BE LIABLE FOR DIRECT, INDIRECT, SPECIAL INCIDENTAL, OR CONSEQUENTIAL DAMAGES ARISING OUT OF THE USE OR INABILITY TO USE THE SOFTWARE OR DOCUMENTATION, EVEN IF ADVISED OF THE POSSIBLITY OF SUCH DAMAGES.

In particular, DGH Corporation shall have no liability for any programs or data stored or used with DGH Corporation software, including the costs of recovering such programs or data.

Copyright (c) 1995, 	DGH Corporation

P.O. Box 5638

Manchester, NH  03108

All rights reserved.

Software License Agreement:

The enclosed materials are provided to you on the express condition that you agree to the following software license provisions. If you do not agree to the following license provisions, promptly return the package and all other materials to your dealer for a refund.

The software and diskette on which it is contained (the "Licensed Software") is licensed to you as the end-user, for your own personal or internal business use. You do not obtain title to the Licensed Software or any

copyrights or proprietary rights in the Licensed Software. You may not transfer, sublicense, rent, lease, convey, copy, modify, translate, convert to another programming language, decompile or disassemble the Licensed Software for any purpose, except as expressly provided for in this license.

You may copy the Licensed Software for backup purposes only, in support of your own use of the software in accordance with the terms and conditions of this license.

Overview:

The enclosed software device driver will interface D1000, D2000, D3000 and D4000 series analog input/output products to LABTECH control software product. The driver provides complete product support for each analog I/O module and the module types can be mixed and matched in any order. The digital I/O capability of each analog I/O module is also accessible thru the driver.

The driver will support from 1 to 124 analog I/O modules connected to one RS-232 serial port.  Each module contains a unique ASCII character address used to identify a module in the system. Each module address value must be entered into the LABTECH software prior to a run-time session. Use the channel "Interface Pt./Channel Number" menu selection to specify a module hardware address. The valid module address, range is decimal 0 to 127 of which four values are not allowed. The four values are decimal 0 (NULL), 13 (CR), 35 (#) and 36 ($). Error checking is provided to detect invalid hardware address values. It is the responsibility of the end-user not to enter such values.

Every module is considered a NORMAL channel in the LABTECH software. Use the LABTECH NORMAL BLOCK menu option to specify each channel type and module address. The driver supported channel types are: Analog Input, Analog Output, Counter, Digital Input, Digital Output, Frequency, RTD and Thermocouple. Each channel entry requires specific hardware information and must be specified prior to a run-time session. Each channel type will be discussed in detail later.

The driver implements a hardware specific command protocol, for reading analog input values and setting analog output values during run-time execution. The protocol is specific to each 1000, 2000, 3000 and 4000

series module. However, each module series uses same communications technique. A command message is first transmitted to a module, then it will respond with data.

The module command structure consists of many two character commands that begin with one prompt character and one address character. The prompt character can be either a '$' or '#'. The '$' prompt requests module data in the simplest form without any communications error checking. The '#' prompt however, requests module data with a two character cumulative checksum.

To ensure the highest level of serial communications data integrity, this driver ONLY supports the '#' prompt. The driver also transmits a two character cumulative checksum with every command which is verified by each module. A BAD CHECKSUM error will be received from any module that detects

a data error in host transmitted command. The data integrity of each response message is also ensured by verification of each received checksum value. If the received data checksum does not compute properly an error message will be generated.

The driver receive routine properly frames each response message by waiting for either either an Asterisk (‘*’) or Question Mark (‘?’) character to be received. These ASCII characters indicate the beginning of a valid DGH module response message has been received. The driver will then read every RS-232 character until a Carriage-Return ($0D) is received. The Carriage-Return character indicates the end of a valid DGH module response message. This receive data technique will ensure that only the valid response message characters are deciphered by the driver. All other received characters will be ignored, such as the echoed command string characters in a RS-232 daisy-chain configuration.

The driver receive data routine also checks each RS-232 character for errors as received. Four different errors can be reported from the RS-232 port: Parity Errors, Framing Errors, Data Overrun and Timeout errors. The first three errors are intuitive. Timeout errors can occur for many reasons including wiring problems, hardware, etc.. From a software point of view, first ensure that the channel address (Interface Pt) value and communications baud rate are correct.  Second, the receive routine within this driver contains a delay loop which waits for characters after each command is transmitted. The delay is required to properly terminate a DGH command/response sequence versus hanging the program while waiting for data.

The amount of time the driver will delay for a response message is user-selectable. Select the LABTECH RS-232 Data Delay value menu selection to specify the RS-232 delay time period. Be sure to enter a time value that is longer than the time to receive a valid response message. Large time values, such as one second, are acceptable for all commands. If a complete response is received within the time delay period, the program will exit out of the delay loop.  If no characters are received within this period of time, the driver will report that no characters have been received and generate a TIMEOUT error for that channel.

Installation Instructions:

Step 1:

Use the LABTECH INSTALL/HARDWARE menu selections to install the DGH module device driver. The LABTECH Notebook or Control software will first prompt with a list selection box that contains all the possible hardware device drivers. Use the mouse to highlight the DGH DRIVER within the Driver Selection list box. Depress the left mouse button to highlight the selection, then depress the ‘Add’ button to activate the driver.

Step 2:

The driver Base Address must be specified before the driver can be used successfully. The Base Address for the DGH device driver determines which serial communications port the LABTECH software will use to communicate with DGH products. The communications port The default hardware base address is defined in the ASCII file DGH.TPL and is 1000 hexadecimal. This address is a 16-bit integer value where each implemented bit controls certain driver functions. If any modifications to the base address must be made, refer to the bit definition table below.

The default base address value specifies RS-232 serial port COM1: and that all Counter channels will be reset at the beginning of each run-time session. Press 'y' now if these parameters are acceptable. Otherwise,

enter 2000H for communications port COM2:, 3000H for communications port COM3: or 4000H for communications port COM4:.

BASE ADDRESS BIT DEFINITIONS

15  14  13  12  11  10   9   8   7   6   5   4   3   2   1   0

|      |     |     |          |     |     |

|      |     |     |          |     |     |

|      |     |     |          |     |     |_______________________  COUNTER CHANNELS

|      |     |     |          |     |                                                          0 = Reset at Run-time

|      |     |     |          |     |                                                          1 = No Reset at Run-time

|      |     |     |          |     |

|      |     |     |          |     |__________________________ D1711, D1712, H1750 support

|      |     |     |          |                                                                0 = No D1711, D1712, H1750 support

|      |     |     |          |                                                                1 = D1711, D1712, H1750 support

|      |     |     |          |

|      |     |     |          |_____________________________ NUMBER OF DIGITAL BYTES

|      |     |     |                                                                           0 = Two bytes of digital data

|      |     |     |                                                                           1 = Three bytes of digital data

|      |     |     |

|      |     |     |                                                                           (8) COM PORT SELECT BITS

|      |     |     |__________________________________ 1 = COM1:, (binary 0001)

|      |     |_____________________________________ 2 = COM2:, (binary 0010)

|      |________________________________________ 3 = COM3:, (binary 0011)

|___________________________________________ 4 = COM4:, (binary 0100)

5 = COM5:, (binary 0101)   *see note below

6 = COM6:, (binary 0110)   *see note below

7 = COM7:, (binary 0111)   *see note below

8 = COM8:, (binary 1000)   *see note below

Note: 	The DGH device driver will technically support upto eight serial communications ports. However,

to select port values [5..8] users must edit the LABTECH program configuration file 	COMPORTS.PRN using a ASCII text word processor. The file must be modified to reflect serial 	port parameters for ports COM5:..COM8:. It is recommended that users contact LABTECH 	directly for instructions.

RS-232 Hardware Connections:

The default communications configuration for LABTECH Notebook Pro 8.0x is for RS-232 three wire communications, without any required external hardware handshaking signals. Meaning, the only connections to make to the host computer serial port are the Ground, Transmit and Receive data lines. This configuration should be used when communicating with DGH modules as they do not require any hardware handshaking signals.

Users familiar with the previous DOS versions of this driver will recall making permanent connections to the RS-232 CTS and DSR input signals for proper operation. This driver does not require these connections to transmit and receive RS-232 data.

Supported Channel Types:

The device driver provides full product support for the D1000 and D2000 series analog inputs with onboard events counters and the D3000 or D4000 series analog output modules. The digital input/output capability within each series is also supported. The analog I/O modules can be mixed and matched in any order with up to 124 modules connected on one RS-232 serial port.

The driver will support 124 each of the analog input, analog output, digital input, digital output and counter input channel types. Each analog I/O module contains one input or output and varying amounts of digital I/O capability. Meaning the driver can control, or monitor, one analog value and many digital I/O points within each module. Using a large quantity of modules, many different I/O points can be controlled or monitored. The only limitations for controlling a large quantity of I/O points is the module address capacity and the number of channels supported in the LABTECH software. The maximum quantity of modules connected to the serial port cannot exceed 124 devices. A discussion on each supported channel type is

located below.

Analog Input

Analog input channels read the present analog data value from any D1000 or D2000 series voltage or current input module. Each D1000 series data value is scaled in millivolts or milliamps. The D2000 series data values are factory scaled in millivolts or milliamperes. However, each D2000 series module has programming capability for linear rescaling of the factory output data values. New transfer functions can also be down-loaded to any D2000 series module.

The data values are read from each voltage module using the Read Data (RD) command. Each value is scaled in either millivolts or milliamps. Meaning that a D1131 +/- 5Vdc input module will return a data value of +04500.00 if positive 4.5 volts were applied. This scaling (4 digits) provides maximum resolution in the fixed data format (+#####.##) used by each module. To convert the millivolt values to volts, or milliamps to amps, within the LABTECH runtime software use "Input Range" setting.

The NORMAL BLOCK analog input channel types (voltage and current) each contain an "Input Range" setting. This setting is used by the driver to normalize data values to volts or amps from millivolts or milliamps. There are seven different input ranges: +/-.01V, +/-.1V, +/-1V, +/-5V, +/-10V, +/-100V and AUTO. The input range values, except +/-100mV and +/-100V, performs mathematical division on each received data value. A divisor value of 1000 used to convert millivolts or milliamps to volts or amps. For

example, a data value of +4500 millivolts can be divided by 1000 by the driver and return +4.5 volts.

The factory calibrated data from each current module is scaled in milliamps. Meaning that a D1251 4-20mA input module will return a data value of +00015.50 when +15.5 milliamps is applied. Select either the +/-100mV or +/-100V input range to  perform no division on the received data value.

The +/-100mV or +/-100V input ranges to return data values as received and perform NO mathematical division. Every other input range will divide the received data value by 1000.

Use the "Interface Pt./Chan Num" menu entry to specify the module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character '1' (31Hex), enter 49 (decimal) as the channel number. The resultant string that will be transmitted by the driver is '#1RD'.

Analog Output

Analog output channels support three different modes of operation: Open-Loop, Closed-Loop and Echo. Each mode can be implemented with any D3000 or D4000 series analog output product. The command utilized by the device driver to transmit data values is the Analog Output (AO) command. As each data value is received from the main LABTECH program it is formatted into a 9 character string value (+#####.##) and transmitted. The output mode for each channel is defined using the LABTECH NORMAL block menu.

Open-Loop analog output channel types each receive their output data values from a disk file. The values required by this device driver must be stored in ASCII real file format. The scaling of each value stored in the file must be equal to the scaling of the analog output hardware receiving these values. For example, a disk value of 4.5 will be output as +00004.50. If this value is intended to indicate +4.5 volts the channel GAIN value can be set for 1000 to output +04500.00 or the disk value should be changed to 4500.

Closed-Loop analog output channel types each receive their data values from an analog input block. Calculations can be performed on the input data value, inside the LABTECH main program, to develop a new output data value. Each properly scaled data value is then output to the analog output hardware.

Each value must be scaled to the values required by the analog output hardware.

Echo analog output channels each receive their data values from an analog input block. The analog input block data values is first received and immediately transmitted to the analog output hardware. The GAIN and OFFSET channel values can be used to rescale the analog input data. Any GAIN and OFFSET scaling is performed inside the main LABTECH program before being output by the device driver.

The data values for each channel type must be scaled to those units required by the analog output hardware. Meaning that each data value transmitted to a D3000 series voltage output module must be scaled in millivolts. Values transmitted to a D3000 series current output module must be scaled in milliamps. For example, a D3000 series 0-10 volt output module must receive a data value of +9000 to properly set the output value to +9.000 volts.

Each D4000 series product contains user-programmable data value scaling. The minimum and maximum full scale values can be re-selected by the user when millivolt and milliamp values are not suitable to the application. It is the end-users responsibility to ensure that the analog output data values are properly scaled to either D3000 or D4000 series products hardware prior to run-time execution.

Use the "Interface Pt./Chan Num" menu entry to specify the analog output module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character 'B' (42 Hex), enter 66 (decimal) as the channel number. The resultant string that will be transmitted by the driver is '#BAO+#####.##', where '+#####.##' is the formatted output data value.

Counter

Counter input channels are used to read the onboard events counter in a D1000 or D2000 series module. Each counter input is incremented on the rising edge of each logic transition from low to high. The counter value can be read as either a cumulative total or incremental value depending on the LABTECH software mode selected.

Cumulative totals are read from any module using the Read Events (RE) command. This mode will allow the counter to increment by one count continually to a maximum value of 9,999,999 counts. Once the maximum value is achieved, the counter will stop counting and must be cleared or reset to resume counting. The counter reset function is not supported within this driver during run-time operations.

Incremental totals are read from any module using the Events Clear (EC) command. The Events Clear command both returns the desired incremental counter value and immediately resets the counter to zero. For high speed counting applications, the incremental counter mode is recommended as the counter will be reset immediately after each value is read.

Using either cumulative or incremental counting mode, each counter channel can be optionally reset (or cleared) at the beginning of every run-time session. The device driver can be configured to reset each counter channel by transmitting the Events Clear (EC) command to each counter module. Any counter residue values returned from a module during run-time initialization will be discarded.

Device driver base address bit #8 controls the counter reset function. If base address bit #8 is set to a logic '0', each counter channel will be reset before every run-time session. If base address bit #8 is set to a

logic '1', the counter channels will not be reset before each run-time session any existing counter residue values will become part of the acquisition run.

Use the "Interface Pt./Chan Num" menu entry to specify the counter input module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character '+' (2B Hex), enter 43 (decimal) as the channel number. The resultant string transmitted to read a cumulative counter channel will be '#+RE'. The resultant string transmitted to read a incremental counter channel will be '#+EC' preceeded by the '#+WE' command.

Digital Input

Digital input channels are used to read the digital input status from any D1000, D2000, D3000 or D4000 analog I/O module. The digital input status values are read using the Digital Input (DI) command and the returned values are typcially two bytes of digital information. However, only the digital information in the second byte is valid and accessible. This data value is returned as an integer value.

Using this Windows dynamic-link library (.dll) driver, additional support has been added to read digital input status from devices that contain two or three bytes of digital information. The D1711, D1712 and H1750 digital products each contain 15, 15 and 24 bits of digital I/O respectively. If all bits were configured as digital inputs, this would require the driver to access either two or three bytes of information. Which is different than the D1000, D2000, D3000 or D4000 series analog I/O modules.

To accomodate the differences between hardware types, two bits in the driver base address have been allocated to enable, or disable support for the D1711, D1712 and H1750 products. One bit enables, or disables the hardware support. The second bit determines whether two or three bytes of information will be read. If two bytes are selected, every D1711, D1712 or H1750 connected must be configured for two bytes. If three bytes are selected, then every D1711, D1712 or H1750 must be configured for three bytes. Please note, the number of bytes returned from either device is user selectable in the hardware setup message. Each device can be configured to output either two or three byte response messages. Please refer to the hardware users manual for more details.

There are 124 possible digital input channels supported by this driver, from which one byte of data can be read. Meaning, in a system that contains 124 analog I/O modules, this software could read the one byte digital input status from each module (along with the analog values). Use the "Interface Pt./Chan Num" menu entry to specify the digital input module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character 'i' (69 Hex), enter 105 (decimal) as the channel number. The resultant string transmitted to read a digital input port will be '#iDI'.

Systems that require support for the D1711, D1712 or H1750 products must have the proper bit set in the driver base address. This mode of operation segments the total 124 digital input channel hardware channel address values into two groups. One group for the analog I/O modules and another for D1711, D1712 and H1750 products. The analog I/O modules that will contain digital inputs must be configured for hardware address values in the range of 1 to 91 decimal. The D1711, D1712 and H1750 module hardware address values must be configured in the range of 92 to 127 decimal. This method of addressing will allow upto 18-D1711, 18-D1712 or 12-H1750 products to be used along with analog I/O modules in any system.

To properly access two bytes of digital input data from either a D1711 or D1712, first and foremost the support for this hardware must be enabled in the driver base address and the module hardware address must be set to a value between 92 and 127 (5C to 7F hexadecimal). Starting at module hardware address 92, each D1711 or D1712 should be configured for address values on each even number from 92 to 126. For example, the first device would be addressed to 92 (5C Hex), the second would be addressed to 94 (5E Hex), etc.. The last device should be addressed to 126 (7E Hex).

Each digital input byte specified by an even numbered module address value is considered the least significant of two bytes received. The most significant digital input byte for each device is accessed by the driver using the next higher odd numbered “Interface Pt/Chan Num” address value. For example, set a  module channel address value to 92 (5C Hex) to access the least significant byte. Then, create another digital input channel and use 93 (5D Hex) as the “Interface Pt/Chan Num” to access the most significant byte. When either “Interface Pt/Chan Num” requires updating, the driver will request data from the module hardware address 92 (5C Hex). The response data will be parsed into two bytes and the proper digital information will be returned  to the channel who required the update (either channel 92 or 93).

To properly access three bytes of digital input data from an H1750, use the same technique as required to access two bytes. Like the two byte technique, specify three sequential “Interface Pt/Chan Num” values starting at 92 (5C Hex). Next, configure the H1750 digital board hardware address for 92 (5C Hex). When either of the three “Interface Pt/Chan Num” values (92, 93 or 94) requires updating, the driver will request data from the digital board hardware address 92 (5C Hex). The three byte response value will be parsed into three separate bytes and the proper digital information will be returned to the channel who required updating (92, 93 or 94). The next H1750 board hardware address would be configured for 95 (5F Hex).

Analog input (D1000 and D2000 series) and output (D3000 and D4000 series) modules always return two bytes of information in response to a Digital Input (DI) command. The digital input data is always located in byte #2. The analog input hardware, depending on the model, will allow access to each bit in the second byte. Check the analog input series for the quantity of usable digital inputs per module. The analog output module hardware supports three digital inputs per device. The valid bit positions are #0, #1 and #2 of the second byte.

The remaining unused digital input bits on any input port are permanently terminated inside each module. The D1000 and D2000 series unused input bits are internally pulled up to +5Vdc and return as logic '1'. The D3000 and D4000 series unused input bits are internally connected to ground and returned as logic '0'.

Set the "Select Bit?" menu entry determines how the digital input data values are read and returned. Select "no" to return the value of the entire digital input byte or select "yes" to return the value of a specific bit.

Use the "Bit Number [0..7]" menu entry to specify which bit number will be read. The valid bit numbers are 0..7 of the second digital input response byte.

Digital Output

The Digital output channels support three different modes of operation: Open-Loop, Closed-Loop and Echo. Closed-Loop and Echo modes each receive their digital output data from analog or digital input type blocks. Open-Loop digital outputs receive their data values from ASCII real formatted disk files. Each data value is transmitted to D1000 or D2000 series products using the Digital Output (DO) command. The data values are each formatted as 8-bit hexadecimal values as mandated by the command protocol.

The D1000 and D2000 series analog I/O modules each contain different amounts of digital output bits, upto eight. The number of bits depends on the analog sensor input type, as some sensors require 2, 3 or 4 analog measurement terminals. The D1701 and D1702 digital I/O modules each contain eight digital outputs. The recently developed D1711, D1712 and H1750 digital I/O product lines however, will support upto 24 individual digital output bits simultaneously. The D1711 and D1712 products each contain 15 bits. The H1750 contains 24 bits. Please refer to the hardware users manual for the correct number of digital output bits in your hardware.

To properly maintain the present status value of all digital output channels, an integer array has been implemented within this driver. Each array position, from 1 to 127, contains an integer data value that represents 8-bits of digital output information. The 127 array positions are accessed via the “Interface Pt/Chan Num” value associated with each digital output channel. The “Interface Pt/Chan Num” value corresponds directly to two values. The first value being the physical hardware channel/module address. The second being the position (or index value) into the integer storage array. For example, the digital module whose hardware address was 31 Hex (49 decimal) would index to position 49 in the integer array. The data value in that location would then be transmitted to the module using the digital output (DO) command.

Analog input (D1000 and D2000 series) modules always require one byte of digital output with the Digital Output (DO) command. Check the analog input series for the quantity of usable digital outputs per module. The integer array contains one position for each digital output of numeric integer type that will store digital output status for each digital output device. The port position in the array is pointed to by the decimal hardware address value. No more than 8 digital output bits can indexed from one internal integer array position.

To properly transmit two bytes of digital output data to either a D1711 or D1712, first and foremost the support for this hardware must be enabled in the driver base address and the module hardware address must be set to a value between 92 and 127 (5C to 7F hexadecimal). Starting at module hardware address 92, each D1711 or D1712 should be configured for address values on each even number from 92 to 126. For example, the first device would be addressed to 92 (5C Hex), the second would be addressed to 94 (5E Hex), etc.. The last device should be addressed to 126 (7E Hex).

Each digital output byte specified by an even numbered module address value is considered the least significant of two bytes transmitted. The most significant digital output byte for each device is accessed by the driver using the next higher odd numbered “Interface Pt/Chan Num” address value. For example, set a  module channel address value to 92 (5C Hex) to access the least significant byte. Then, create another digital input channel and use 93 (5D Hex) as the “Interface Pt/Chan Num” to access the most significant byte. When either “Interface Pt/Chan Num” requires updating, the driver will convert both integer values to 8-bit hexadecimal values, convert them to ASCII characters and transmit them using the Digital Output (DO) command to module hardware address 92 (5C Hex).

To properly access three bytes of digital output data on a H1750, use the same technique as required to access two bytes. Like the two byte technique, specify three sequential “Interface Pt/Chan Num” values starting at 92 (5C Hex). Next, configure the H1750 digital board hardware address for 92 (5C Hex). When either of the three “Interface Pt/Chan Num” values (92, 93 or 94) requires updating, the driver will convert the three integer values to 8-bit hexadecimal values, convert them to ASCII and transmit them using the Digital Output (DO) command to H1750 hardware address 92 (5C Hex). The next H1750 board hardware address would be configured for 95 (5F Hex).

Both the Closed-Loop and Echo digital output modes use the internal array. Before each new digital output bit status is transmitted, the new bit status is logically integrated with the present bit status stored in the

array. The resultant value is then transmitted to the correct digital output port and stored in the array buffer. Open-Loop digital outputs receive their values from disk files and each file value updates all 8-bits.

Therefore, there is no reason to maintain the status of each port.

Open-Loop digital outputs receive their data values from a disk file. Each value is used to control all 8 bits of a digital output port. The file format is discussed in the LABTECH software users manuals in great detail.

Each data value is read, formatted into a two character hexadecimal value and transmitted by the driver. The data values control the entire 8-bits of a digital output port. Therefore, the status of each individual output bit will be altered as the new values are transmitted. Open-Loop digital output status values are not stored in the driver array buffer before being transmitted.

Closed-Loop digital outputs can be configured as alarm outputs or on-off outputs. The data required to update a Closed-Loop digital output is received from an analog input channel. The analog input block data is checked against preset alarm/limit values and the proper output bit status is determined. Both a HI and LO alarm/limit value should be specified for proper operation.

Echo mode digital outputs receive their input data from a analog or digital input block. Typically, a digital input block. The functional operation of each Echo mode digital output bit versus the received digital input state is complementary. Each D1000 or D2000 series digital output is an open-collector transistor. Each transistor is turned 'on' by setting the proper bit in the digital command to a logic '1'. For example, to turn 'on' bit DO0/LO with the Digital Output command transmit the following string of characters, '$1DO01'. Transmit a logic '0' with the Digital Output command to turn 'off' a digital output bit.

The hardware digital output bits will immediately turn 'on' when the data from any input block is a logic '1'. The received logic '1' will then cause the digital output transistor to sink current and the collector voltage

will go to ground (zero volts). Therefore, the input block logic levels received will cause an complimentary, or opposite logic affect on a digital output hardware terminal.

Use the "Interface Pt./Chan Num" menu entry to specify the digital output module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character 'i' (69 Hex), enter 105 (decimal) as the channel number. The resultant string transmitted to set a digital output port will be '#iDOxx', where xx is the two character hexadecimal port value.

Frequency

Frequency input channels read the present frequency or pulse-width data from a D1600 or D2600 series frequency or timer input. The data values read from any D1600 or D2600 series product using the Read Data (RD) command and returned in floating-point data format. The D1600 series values are scaled inside each module to either Hertz or Milliseconds. The D2600 series data values are factory scaled to Hertz or milliseconds and can be rescaled by the end-user to values more applicable to the application. It is the

responsibility of the end-user to determine and keep track of scaled units for data values received from any D2600 series product.

Use the "Interface Pt./Chan Num" menu entry to specify the frequency input module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character 'i' (69 Hex), enter 105 (decimal) as the channel number. The resultant string transmitted to read a frequency input channel will be '#iRD'.

RTD

RTD input channels read the present temperature data from any D1400 series RTD input product. The temperature values are read using the Read Data (RD) command and returned in floating-point data format. The floating-point data is scaled in either degrees Celcius or Fahrenheit. The temperature scaling is performed inside each module and is user-selectable within the module setup message.

Use the "Interface Pt./Chan Num" menu entry to specify the RTD input module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character 'i' (69 Hex), enter 105 (decimal) as channel number. The resultant string transmitted to read a RTD input channel will be '#iRD'.

Thermistor

Thermistor input channels read the present temperature data from any D1400 series thermistor input product. The temperature values are read using the Read Data (RD) command and returned in floating-point data format. The floating-point data is scaled in either degrees Celcius or Fahrenheit. The temperature scaling is performed inside each module and is user-selectable within in the module setup message.

Use the "Interface Pt./Chan Num" menu entry to specify the thermistor input module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character 'i' (69 Hex), enter 105 (decimal) as the channel number. The resultant string transmitted to read a thermistor input channel will be '#iRD'.

Thermocouple

Thermocouple input channels read the present temperature data from any D1300 series thermocouple input product. The temperature values are read using the Read Data (RD) command and returned in floating-point data format. The floating-point data is scaled in either degrees Celcius or Fahrenheit. The temperature scaling is performed inside each module and is user-selectable within the module setup message.

The thermocouple input type menu selection may be specified but is not manditory. Since the thermocouple linearization and Cold Junction Compensation (CJC) are performed inside each module, the type is not critical. No linearization files or tables are required for thermocouple input channels. The linearized data values returned from each module are already scaled in actual degrees C or F.

Use the "Interface Pt./Chan Num" menu entry to specify the thermocouple input module hardware address. Enter the decimal equivalent of the ASCII character address. For example, if the module address is ASCII character '<' (3C Hex), enter 60 (decimal) as the channel number. The resultant string transmitted to read a thermocouple input channel will be '#<RD'.

Un-supported Driver Channel Types:

The following list of six channel types are not supported by this software device driver. A strain, or bridge, input channel type is not supported by the D1000 and D2000 product families. Select the Analog Input channel type to acquire data from the DGH Bridge input products. The analog input values returned will be in floating point data format.

Strain Measurement

Resistance Measurement

Pulse Output

RS-232 Input

GPIB Input

GPIB Output

Error Reporting:

The device driver provides extensive error checking during each run-time session. System and module level error messages are detected and displayed as they occur. System level errors will normally occur during run-time initialization. These errors can occur while accessing disk files or initializing module hardware.

Module errors are detected throughout each run-time session. All received error messages will cause a displayed message to appear that describes the present module error. If error messages persist, exit the run-time environment and determine the cause of the problem. One example of a long term persistant problem would be to define a counter input channel on a D3000 or D4000 series product. The module COMMAND ERROR message would be returned continuously until the channel address was reselected. Only D1000

and D2000 series products contain counter inputs.

The STATUS value displayed with each error message contains the decimal equivalent of the module hardware address that caused the error. This value can be used to quickly determine where the error was generated and why.

Module Errors

The device driver can detect every possible error message returned from a D1000, D2000, D3000 or D4000 series product. Each received error message causes the driver to return both an error code and error description. The error codes are always negative numeric values and each description is displayed on the screen. Refer to the hardware users manual for a detailed description of each module(s) error.

-1: “Address Error”

-2: “Bad Checksum Error”

-3: “Command Error”

-4: “Limit Error”

-5: “Manual Mode Error”

-6: “Not Ready Error”

-7: “Digital Output Error”

-8: “Parity Error”

-9: “Syntax Error”

-11: “Value Error”

-12: “Write protected Error”

Device Driver Errors

Twenty other error messages can be reported from directly inside the driver software. These errors are only generated during run-time sessions when the driver detects a specific system problem. Once a system problem is detected, both the negative error code and description will be displayed. A complete list of driver error codes and descriptions is listed below. Notice that the error message descriptions are intuitive as to the problem detected.

Note:	All error messages that refer to the LABTECH COMPORTS.PRN configuration file are valid only 	in the DOS version of this device driver. These messages will not be displayed in the Windows 	.DLL device driver.

-10: “Hardware TIMEOUT Error. Device is not responding!”

-13: “Received checksum is incorrect”

-14: “Device driver does not support this channel type”

-15: “Digital input response message is to short for selected channel”

-16: “Driver error opening file COMPORTS.PRN, File Not Found!”

-17: “Driver error reading file COMPORTS.PRN!”

-18: “Driver error, unexpected end of COMPORTS.PRN file!”

-19: “Driver error, COMPORTS.PRN file has NO COMx: ports selected!”

-20: “Driver error, Invalid driver base address value!”

-21: “Driver error, Requested WIN-COM#: is not specified in COMPORTS.PRN”

-22: “Driver error, Invalid channel address specified (0, 13, 35 or 36)”

-23: “Driver error, Cannot specify 7 DATA BITS with NO PARITY on RS-232 Port”

-24: “Invalid COMx: port specified in base address, values must be 1xxx-4xxx”

-25: “.DLL error, Error occurred during transmission of a command character”

-26: “.DLL error, UART Data Overrun Error detected”

-27: “.DLL error, UART Parity Error detected”

-28: “.DLL error, UART Framing Error detected”

Driver Development Kit (DDK) Errors

162 : “INTNUM is not set.  Be sure that the link DDK_INTNUM=X, where X \n\

is the hex interrupt number, has been added to your LTN.CNF file.”

163 : “The TSR DDK driver is not loaded, not found, or attemps to use \n\

the wrong interrupt number.  Also be sure that the DDK_INTNUM=X \n\

has been added to your LTN.CNF file, where X = hex interrupt number.”

164 : “DDK version error”

Troubleshooting Problems/Performance Optimizing Hints

1. 	DISABLE the 'ser_view' RS-232 debugger option in the LTN.CNF file. This option will slow down 	the communications port throughput at higher sampling rates and possibly cause program runtime 	errors.

2. 	Mouse movement, from a serial mouse, can cause trend graph disturbances during runtime 	execution of the Microsoft Windows version of Notebook.

Install a COMx: port board that contains a 16550A UART or locate a UARTand install it on the 	existing COM board.

3. 	DISABLE the 'LINEFEEDS' option in each module setup message. If this option is enabled, 	possible Timeout and runtime error messages can occur.

4. 	Communications port settings such as baud rate, parity and number of data bits and stop bits must 	be set to the same settings as the connected modules. If parity is not specified in the modules the 	select 8 data bits, no parity and one stop bit. With either even or odd parity selected, choose seven 	data bits and one stop bit.

5. 	Ensure that both software switches “cts_wait” and “dsr_wait” are not specified in the LTN.CNF 	file. If they are, set both switches equal to “No”.

Trademarks

IBM is a trademark of International Business Machines Corporation.

LABTECH is a registered trademark of Laboratory Technologies Corporation.

Microsoft Windows is a registered trademark of Microsoft, Corporation.

MS-DOS is a registered trademark of Microsoft, Corporation.