Hadron dipole polarity reversal procedure/checklist

By Scot Spiegel and Mark Stevens

Revision: March 27, 1998

Persons performing procedure: ________________________________________________date________

This procedure/checklist outlines the physical switching of the Hadron dipole main current lead cables and the polarity reversal of all related equipment.  It is intended to be performed by qualified Jefferson Lab technicians who have been trained to perform it by the Hall A technical staff.

Note:

The Hadron dipole is in normal (Hadron) polarity when the positive main current lead cables (identified by red tape) are landed on the positive output of the power supply (contact A POSITIVE), and on current lead A of the magnet (identified as the left-hand lead when you are sitting on Q3 and looking at the top of the dipole cryostat).

# Danger

The Hadron dipole is a low-voltage, superconductive magnet system capable of storing lethal amounts of power.  Because of an installed “freewheeling” or “persistent” switch, this energy storage capability of the magnet can exist under certain conditions  even when the power supply is turned off.  You must be extremely careful to ensure that all energy has been extracted from the magnet system prior to breaking the main current circuit connections.  Failure to do so could result in death or severe injury to the person breaking the connection.

- The Hadron dipole Dynapower power supply, designated PD172, can only be operated in the 	remote control mode, by using the Hall A EPICS control software.  The power supply must be 	ramped down to 0 amps DC, +/- 1 amp DC as read from the DC CURRENT meter on the front 	of the Dynapower power supply.  If the magnet is at or near its maximum field, this step can 	take hours to complete.

- Verify the completion of step 1 by observing a reading of  000 or 001 amps in the DC 	CURRENT meter on the front of the Dynapower power supply, PD172.

- Place a clamp-type DC amp meter on one of the large (535 MCM) main current leads 	between 	the Dynapower and the magnet.

## Danger

### Place the clamp-type DC amp meter only on one of the cable(s) between the Dynapower

### and the magnet, not between the Dynapower and the dump resistor cabinet.  These correct cables can be located by the markings on top of the Dynapower, and by observing that two sets of 5 cables each lead from the Dynapower to the magnet; these cables are landed on A POSITIVE and B NEGATIVE.

Verify a reading of 0.0 amps DC on the clamp-type DC amp meter.  With the clamp meter in 	place, make a test circuit with a short piece of at least 22 awg wire and a D-cell flashlight battery.  	Pass a loop of wire through the amp meter and connect it to the flashlight battery.  You should be 	able to see a current of several amps DC with this test setup.  After verifying the operation of the 	amp meter, again observe a reading of 0.0 amps DC.

- Verify a reading of 0.010 VDC or less on the QUENCH PROTECTION CONTROLLER,

located in rack OD172Q.  This meter reads the voltage across the main current leads at the 	 		magnet.  Any significant difference of potential means that a significant current is still  	  		flowing.

- If all of the previous steps have been successfully completed, the magnet has been completely 	discharged, and is now safe to disconnect for polarity reversal.

Danger

The Dynapower power supply PD172 is supplied with uninterruptible 480VAC 3 phase

power and uninterruptible 120VAC single phase power.  Compliance with the

following steps mitigates these hazards.

- Turn off the main input power switch on the front of the Dynapower power supply, PD172, a 	large lever-type switch with a red and black handle on the right side of the front panel.

- Turn off the power to the Dynapower at the safety disconnect switch marked PD172  DIPOLE 	MAGNET SAFETY DISCONNECT SWITCH, and lock it out in accordance with Jefferson Lab 	safety lockout procedures.

- Unplug the 120VAC plug which provides uninterruptible power to the Dynapower.  This plug is 	located inside rack OD172Q, is plugged into a rack-mount uninterruptible power supply, and is 	marked by a CEBAF caution tag “CAUTION – Uninterruptible control power for the Hadron 	Dipole power supply – do not disconnect”.  Lock out the plug in a suitable plug lockout box in 	accordance with Jefferson Lab safety lockout procedures.  Verify no status/annunciator lights are 	lit on the front of the Dynapower.

- Disconnect and swap the magnet main current leads at the power supply.  Tools & materials 	required are: Two ¾” combination wrenches, 3/4” socket wrench.

- Change the plugs on the current limiting resistor box to the correct box for the polarity you are 	changing to.  The boxes are marked “normal (Hadron) polarity” and “reverse (electron) polarity”.  	Ensure both cables are plugged into the same box.

- Change the polarity of the Field Gradient Compensating Coils for the Dipole NMR probe on the 	back of the Kepco power supply located in rack 1H72B06 .  Disconnect the Kepco power supply 	from AC power by pulling its plug.  Follow the instructions on the top of the back of the Kepco 	for the appropriate polarity.  Plug the Kepco back in, and make sure it is turned on!

- Change the polarity of the Dynapower remote voltage sense.  Move the concrete and lead 	shielding in front of the Dynapower, observing proper lead handling technique (using gloves).  	Open the front door of the Dynapower to expose the controls closet.  About 3’ from the floor 	there is a black on yellow label tape which contains the instructions to reverse the voltage sense 	wires number 280 and 281.  Land the wires on the appropriate lugs for the polarity you are 	changing to, according to the instructions.  Close the door and restore the shielding.

- Unlock and restore power to the Dynapower power supply.  Reset faults and test for proper 	operation.