1. Define the scope of work

- Job Summery

Install new supply and return L.C.W. 2” lines to Big Bite power supply.

Install new valve and regulator

- Affected systems

L.C.W. 	cooling system

Big Bite power supply

2. Analyze Hazard

| Task location Hall-A | Installation of Big Bite L.C.W. Lines |
| --- | --- |
| Division Physics | Prepared by Dezern |
| Department Hall A | Reviewed by Folts |
| Supervisor Folts | Approved by |
| Standard Requirements: (PPE, TOSPs, SOPs, etc.) |  |

| Task | Potential Hazards | Risk Code before mitigation | Safe Procedures/Practices/Controls | Risk Code after mitigation |
| --- | --- | --- | --- | --- |
| Install new supply and return L.C.W. 2” lines to Big Bite power supply. Install new valve and regulator | Crane Crush, Bump, Pinch Drop load Cutting, grinding, welding Fall | 3 3 2 | Correct rigging, Minimum elevation Clear area of personnel and equipment Use steel toed shoes and safety glasses Use warning beacons and guards when appropriate Use hard hats when deemed necessary Equipment specific training Proper PPE, Crane Use of welding screens and helmet Ladder training, harness training and a harness when necessary | 1 1 0 |

3. Develop and implement Hazard controls

- List of PPE

Hard Hat

Gloves

Eye protection

Safety Shoes

Welding  Shield

Fire extinguisher

Harness

Fire blanket

- Identify danger zones

Weld flash/burn

Falling load/objects

Load control

Pinch points

Crush zones

- Training required

Welding

Fire watch

Ladder

Crane

Power hand tools

Fall protection training											Equipment specific training

Lock-out, Tag-out

Spill prevention

4. Perform work within controls

- Number of people needed

1-person rig and fit,1-crane,1-fire watch,1-welder

- Verify  that needed training is completed and current

- List of materials

Welding machine

Grinder

Slings

Shackles

Hand tools

Drawings

2”pipe

Valves

Flow regulator

Pipe hangers

Ladders

- Procedure

Perform pre-job briefing.

Lock-out, Tag-out Big Bite power supply.

Set up equipment, welding machine, screens, ladders

Cover wire over racks with fire blanket, grind paint from over head beam and weld unistrut to beam .Cut 2”pipe to length and install using crane to lift sections and  mount to pipe hangers.

Set up argon purge on line to be welded.

Install prefabricated sections of pipe, downdrafts to overhead lines and weld.

Install valve and flow regulator and flex hose with couplings.

Close supply and return L.C.W. valves and lock out and tag.

Drain both lines.

Cut 5” section out of both lines and install prefabricated 2” pipe “T” sections and weld.

Connect flex hose with coupling to B.B. power supply.

Torque bolts on valves as per specification.

Take locks off valves and turn water on to system.

Check for leaks in system.

Set flow regulator to specified pressure.

- Post job briefing and cleanup

Clean and store all tools and machines.

Sweep and clean floor, racks, balcony.

Roll up used 1”rubber lines and store in proper place.

5. Provide feedback and continuous improvement.