|  |  | TITLE: | ES&H Manual |
| --- | --- | --- | --- |
| DOCUMENT ID: | 3310 Appendix T2 Operational Safety Procedure Form |  |  |

|  | Serial Number: |  |  |  |  |  |  |  |  |  |  | [Enter Serial Number] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  | (Assigned by ESH&Q Document Control x7277) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | X | OSP |  |  |  |  |  |  | TOSP |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | *Attach the Task Hazard Analysis (THA) related to this procedure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Issue Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Expiration Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (No more than three years from Issue Date except TOSP which is three months from issue date) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Title: |  | Hall A Left Dipole Polarity Reversal Procedure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Location: |  |  |  | Hall A |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Risk classification (See ESH&Q Manual Chapter 3210 Appendix T3 Risk Code Assignment.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Without mitigation measures (3 or 4): |  |  |  |  |  |  |  |  |  | 4 |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | With mitigation measures in place (0, 1, or 2): |  |  |  |  |  |  |  |  |  | 1 |  |  |  |
|  | Document Owner(s): |  |  |  |  |  |  |  | Folts |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  | 10/12/10 |  |  |  |  |  |  |  |  |  |
| Supplemental Technical Validations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Hazard Reviewed (per ES&H Manual 2410-T1): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Subject Matter Experts Signature: |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  |  |
|  | Power supplies / Howard Smith |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | [Enter Hazards] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | [Enter Hazards] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Approval Signatures: |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Print Signature |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |  |
|  | Division Safety Officer: |  |  |  |  |  |  |  |  | Dennis Skopik |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Department or Group Head: |  |  |  |  |  |  |  |  |  |  |  |  | Kees deJager |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Safety Warden of Area: |  |  |  |  |  |  |  |  |  | Ed Folts |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Other Approval(s): |  |  |  |  |  |  | Jack Segal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Document History: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Revision: |  |  | Reason for revision or update: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Serial number of superseded document |  |  |  |  |  |  |  |  |  |  |
|  | [Rev] |  |  | [Enter Reason] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | [Previous Rev] |  |  |  |  |  |  |  |  |  |  |

Distribution: Copies to: affected area, authors, Division Safety Officer, ESH&Q Document Control

After expiration: Forward original and log sheet of trained personnel to ESH&Q Document Control.

|  | - Purpose of the Procedure |  |  |
| --- | --- | --- | --- |
|  | This OSP will describe the hazards associated with the polarity reversal of the Hall A left dipole power supply and establish the measures required to mitigate the hazards. |  |  |
|  | - Scope – include operations, people, and/or areas where procedure applies |  |  |
|  | This procedure will be accomplished inside Hall A, on the left spectrometer. The power supply is mounted on the power supply platform. The Hall A run coordinator or the Hall A Work coordinator shall be informed before the procedure is accomplished. An entry shall be made into the Hall A logbook that a polarity change has taken place and what the new polarity is. |  |  |
|  | - Description of the Facility: (include floor plans and layout of a typical experiment or operation) |  |  |
|  | The Hall A left dipole polarity reversal switch is a manual switch located in an electrical enclosure on top of the left dipole Dynapower power supply. The Dynapower power supply has two sources of power. The power supply and the magnet it’s self. This magnet can store a lethal amount of energy. This procedure mitigates the hazards involved in the operation of this manual switch. The Hall A left dipole polarity reversal switch is a manual switch located in an electrical enclosure on top of the left dipole Dynapower power supply. The Dynapower power supply has two sources of power. The power supply and the magnet it’s self. This magnet can store a lethal amount of energy. This procedure mitigates the hazards involved in the operation of this manual switch. |  |  |
|  | - Authority and Responsibility: |  |  |
|  |  | 4.1 Who has authority to implement/terminate |  |
|  | Hall A electrical workers |  |  |
|  |  | 4.2 Who is responsible for key tasks |  |
|  | [Start Typing Here] The Person In Charge is responsible for implementing the provisions of this OSP. The Person In Charge is also responsible for the following: - Responsible for the subject equipment being under configuration control via Lock, Tag and Try (LTT) when the equipment is opened. II. Responsible for ensuring that only the personnel performing the procedure are inside the hazard boundary at the top of the stairs. III. Responsible for completing a written checklist of the procedure and making a logbook entry. This OSP also designates Authorized Polarity Reversal Personnel. Qualified assistants may be any Hall A electrical worker. |  |  |
|  | - Who analyzes the special or unusual hazards (See ES&H Manual Chapter 3210 Appendix T1 Work Planning, Control, and Authorization Procedure) |  |  |
|  | Electronics coordinator – Jack Segal Hall coordinator – Ed Folts Equipment owner - Howard Smith |  |  |
|  | - Personal and environmental hazard controls including: |  |  |
|  |  | 6.1 Shielding |  |
|  | Hazard boundary at the top of the stairs of the power supply balcony. |  |  |
|  |  | 6.2 Interlocks |  |
|  | VVU |  |  |
|  |  | - Other |  |
|  | The hazards associated with working on this power supply are as follows: - The input power to this unit is 480VAC, supplied through a safety disconnect located next to the unit and 120VAC supplied from an uninterrupted power supply in or near the dipole instrument rack. The power is supplied from circuit breakers located in the 480VAC panel and the 120/208VAC panel on the side of the spectrometer. Electrical and arc blast hazards exist when the doors or panels of the unit are open and the unit is on. Consequence level: IV. Likelihood code: B. Risk code: 3. Mitigated risk code: 1. - The output of the power supply can be up to 10VDC at 2000A. The voltage on the output circuit can temporarily be as high as 270VDC during a magnet quench. This is an electrical hazard to persons near the current carrying circuit elements. Consequence level: IV. Likelihood code: B. Risk code: 3. Mitigated risk code: 1 - The magnet system can store more than 2 megaJoules of electrical energy in a certain mode even when the power supply is off. Consequence level: IV. Likelihood code: B. Risk code: 3. Mitigated risk code: 1 - The 480VAC input power safety disconnect switch, and the 120VAC power must be locked out using LTT procedures by all persons working inside the polarity reversal switch box.. When a polarity change is performed, an Arc Flash Hazard Boundary and an Electrical Shock Hazard Boundary will be established around the unit by closing the access gate at the entrance to the power supply platform. Only authorized personnel with required PPE will be allowed inside the boundary. - The power supply output must be turned off by following the checklist procedure before access is allowed to the polarity reversal switch. - The magnet stored energy must be dissipated by following the checklist procedure before access is allowed to the polarity reversal switch. |  |  |
|  | - Monitoring systems |  |  |
|  | Hall A EPIC controls |  |  |
|  | - Ventilation |  |  |
|  | NA |  |  |
|  | - List of safety equipment (i.e: personal protective equipment or special tools) |  |  |
|  | Safety glasses or goggles, rubber safety mat rated at least 500V, rubber high voltage (500V) gloves with leather outer gloves, long sleeved cotton or fire retardant shirt, long fire retardant pants, closed-toe shoes and a hardhat with attached Hazard Risk Category 2 Arc Flash Face shield rated at 15cal/cm. |  |  |
|  | - Associated administrative procedures |  |  |
|  | Attached procedure |  |  |
|  | - Operating guidelines |  |  |
|  | As per the Hall A operating manual |  |  |
|  | - Notification of Affected Personnel (How and Who) |  |  |
|  | Hall A experimenters via HAlog |  |  |
|  | - List of steps required to execute the procedure from start to finish. |  |  |
|  | Left Dipole polarity reversal procedure/checklist Person in charge: ____________________________________ date:______ The person in charge is responsible for the proper execution of this checklist. This procedure/checklist outlines the physical switching of the Left Dipole main current polarity reversal switch and the polarity reversal of all related equipment. These persons will be exposed to potential electrical hazards during the performance of this checklist. While this checklist is being executed, no other work is allowed within the hazard boundary. Only Lock, Tag and Try trained personnel will be allowed to perform a polarity change. Note: The Left Dipole is in (-)(electron) polarity when the polarity reversal switch handle is in the up position, and in (+)(hadron) polarity when the polarity reversal switch handle is in the down position. The convention for all of the polarity switches/boxes is to match the positions of the devices (i.e., all handles/connectors in the up position = electron polarity). # Danger The Left Dipole is a low-voltage, superconductive magnet system capable of storing lethal amounts of energy. Energy can be stored even when the power supply is turned off. You must be extremely careful to ensure that all energy has been extracted from the magnet system prior to moving the polarity reversal switch to a different position. Failure to do so could result in death or severe injury to the person moving the switch. - Set the power supply current to 0 amps DC, +/- 1 amp DC as read from the DC CURRENT meter on the front of the Dynapower power supply. 2.____ Check that both the M3 and M4 lamps are lit on the front of the Dynapower power supply, PD171. Note M3 indicates that the power supply output is turned on. If the lamp is off, the power supply may simply be turned off (no output). This can be verified by the software control screen, and by using the LAMP TEST switch on the front of the Dynapower. M4 indicates that the system is in slow – dump mode. If M4 is already extinguished, the system may be in fast – dump mode already For the purposes of this procedure, ensure that both M3 and M4 are lit, or verify that the lamps work by pressing the LAMP TEST switch. 4.____ Verify that the DC CURRENT meter on the front of the Dynapower power supply reads 000 or 001. 3.____ Place the magnet system in the fast dump mode by performing a hard reset on either of the helium lead flow controllers located in rack 0D171Q: To do this, remove the bezel guard, press the menu button, and then press the reset button. Be sure to replace the bezel guard. The Dynapower’s output should now be off, and the system should be in fast – dump mode. On the front of the Dynapower, observe a quench protection fault, and both the M3 and M4 lamps extinguish. 5.____ The Shock Protection Boundary and the Flash Protection Boundary shall now be established by closing the “Danger – restricted area” signed gate at the entrance to the power supply platform. All work shall be accomplished within this boundary except for step 18. 6.____ Prior to turning off power to the power supply verify that the Voltage Verification Unit (VVU) is operational by moving the phase switch and observing the voltage meter is reading a voltage in all three phases of 480VAC. If the VVU meter does not correctly read all of the voltages, stop and contact the system owner or the Hall coordinator. 7.____ Turn off the main input power switch on the front of the Dynapower power supply, This is the large lever-type switch with a red and black handle on the right side of the front panel. 8.____ Turn off the DIPOLE MAGNET SAFETY DISCONNECT SWITCH marked and lock it out in accordance with Jlab Lock, Tag and Try (LTT) procedures. The person in charge and all other persons that will physically touch the polarity reversal switch shall lock out the switch in accordance with Jlab Lock, Tag and Try (LTT) procedures. 9.____ Verify the lack of 480VAC by selecting all three phases on the VVU and reading 0 VAC. Note The minimum personal protective equipment used shall be safety glasses or goggles, a rubber safety mat rated at least 500V, rubber high voltage (500V) gloves with leather outer gloves, long sleeved cotton or fire retardant shirt, long fire retardant pants, closed-toe shoes and a hardhat with attached Hazard Risk Category 2 Arc Flash Face shield rated at 15cal/cm. ## Danger ### Place the clamp-type DC amp meter on one of the cables between the Dynapower polarity reversal switch and the magnet, not between the Dynapower and the dump resistor cabinet. The correct cable can be found in the cable tray marked “>>TO MAGNET>>”. It is wrapped with red tape, and on the red tape appear the words “PUT CLAMP METER HERE”. 11.___.Inspect the clamp-type DC amp meter for serviceability prior to use. Turn on the clamp- type DC amp meter by turning the rotary switch to the 200A range, and with the meter operating in free air (nothing in the clamp jaws) adjust the meter to read zero amps DC. Taking great care not to bump or accidentally mis-adjust the zero setting, place the clamp-type DC amp meter on one of the large (535 MCM) main current leads between the Dynapower and the magnet. Ensure that the jaws of the clamp are completely closed and the meter is turned on to its lowest DC range Verify a reading of 0.0 amps DC on the clamp-type DC amp meter. 12.___ With the clamp meter in place, make a test circuit with a short piece of at least 22 awg wire and a 1.5v flashlight battery. Pass a loop of wire through the amp meter and connect it to the flashlight battery. You should be able to see a current of several amps DC with this test setup. After verifying the operation of the amp meter, again observe a reading of 0.0 amps DC. 13.___Position an electrical safety mat rated at 500V or more behind the power supply, below the polarity reversal switch door. Put a fiberglass ladder on top of the mat. 14.___Verify the proper operation of the DC voltmeter by measuring the voltage from a 1.5v battery. 15.___ Unlock and open the polarity reversal switch door. Place the DC voltmeter, (set to read milli-volts, typically the 300mV switch position) across the center contacts of the switch (across the moving handle pivot points). In this step you are reading the voltage drop (if any) across the dump resistor from any current which may be flowing through it. Any significant difference of potential means that a significant current is still flowing. Observe a reading of 10mVDC or less. If the voltage is higher than 10mV, and the voltage is decreasing, the magnet is still discharging. You must wait until the voltage is 10mVDC or less! 16.___If all of the previous steps have been successfully completed, the magnet has been sufficiently discharged, and is now safe to proceed with polarity reversal. 17.___ Using at least an 18 gauge wire (a meter-lead type wire is fine) and alligator clips, short across the polarity reversal switch from pivot point to pivot point. This is a safety device which provides a path for several amps of current if for any reason all of the previous precautions overlooked 10 amps or less in the magnet. With the shorting jumper in place, move the polarity reversal switch to the new position. Remove the shorting jumper. Make sure all tools and meters are removed. Close and lock the switch box. 18.___ PPE may now be removed. Change the plugs on the current limiting resistor box to the correct box for the polarity you are changing to. The boxes are marked “ (Electron) polarity” and “reverse (Hadron) polarity”. Ensure both cables, labeled P1 and P2, are plugged into the same box. 19.___Change the polarity of the Field Gradient Compensating Coils for the Dipole NMR probe by first turning off the Kepco power supply in rack 1H71B06 and then moving the Field Gradient Compensating Coil Polarity Reversal Switch, located in the same rack, to the appropriate position. The convention for all of the polarity switches is to match the positions of the switches (i.e., all handles in the up position = electron polarity) Make sure the Kepco is turned back on! 20.___ Unlock and restore 120VAC uninterruptible power to the Dynapower power supply. 21.___ While wearing the minimally required PPE, which is safety glasses and a long sleeved cotton shirt, unlock and restore 480VAC power to the Dynapower power supply. Turn on lever-type switch on the power supply. Ensure that all tools and supplies that belong in the polarity reversal tool box are put back into it, and that the meters and source are turned off. 22.___Using Hall A EPICS software, or local controls, reset faults and test for proper operation. Ensure that you leave the Dynapower in remote control mode. |  |  |
|  | - Back out procedures, i.e., steps necessary to restore the equipment/area to a safe level. |  |  |
|  | Notify system owners- Jack Segal or Howard Smith |  |  |
|  | - Special environmental control requirements: |  |  |
|  | NA |  |  |
|  | - Environmental Impacts (See EMP-04 Project/Activity/Experiment Environmental Review |  |  |
|  | NA |  |  |
|  | - Abatement Steps – Secondary Containment, or Special Packaging requirements |  |  |
|  | NA |  |  |
|  | - Training requirements |  |  |
|  | Electrical worker qualification |  |  |
|  | - Unusual/Emergency procedures e.g., Injury, Fire, Loss of power |  |  |
|  | NA |  |  |
|  | - Instrument calibration requirements, e.g., safety system/device recertification, RF probe calibration |  |  |
|  | NA |  |  |
|  | - Inspection schedules |  |  |
|  | NA |  |  |
|  | - References/Associated Documentation |  |  |
|  | NA |  |  |
|  | - List of Records Generated (Include Location / Review and Approved procedure) |  |  |
|  | HAlog |  |  |

Authorized/Trained Individuals

| Print Name/Signature | Date |
| --- | --- |
| Jack Segal |  |
| Heidi Fansler |  |
| Jeffry Ewing |  |
| Howard Smith |  |
| Jessie Butler |  |
| Ed Folts |  |

|  | ISSUING AUTHORITY | APPENDIX AUTHOR | APPROVAL DATE | EFFECTIVE DATE | EXPIRATION DATE | REV. |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | ESH&Q Division | Harry Fanning | 10/05/09 | 01/01/10 | 10/05012 | 0 |  |  |

This document is controlled as an on line file.  It may be printed but the print copy is not a controlled document.  It is the user’s responsibility to ensure that the document is the same revision as the current on line file.  This copy was printed on 7/29/2026.