1. Define the scope of work  
	Clean fans and heat sinks inside Q1 power supply ZFCT control box.

2.  Analyze Hazard

| Task | Potential Hazards | Risk Code before mitigation | Safe Procedures/Practices/Controls | Risk Code after mitigation |
| --- | --- | --- | --- | --- |
| Remove ZFCT control box and clean fans/heat sinks | Electrical flash, shock hazard Radioactive contamination hazard | 4 3 | Lock, Tag and Try the source of electrical energy in accordance with the power supply SOP before testing switch In accordance with the standing Radiation Work Permit, Radcon personnel will survey the dust present for radioactive contamination and if required write a Radiation Work Permit | 1 0 |

3. Develop and implement Hazard controls
	Lock, Tag and Try the source of electrical energy in accordance with the power supply SOP before testing switch

In accordance with the standing Radiation Work Permit, Radcon personnel will survey the dust present for radioactive  contamination and if required write a Radiation Work Permit

4. Perform work within controls (follow procedure)

- Summary of job

  - Clean fans and heat sinks inside Q1 power supply ZFCT control box.

- List of PPE

  - Safety glasses or goggles, a rubber safety mat rated at least 500V, rubber high voltage (500V) gloves with leather outer gloves, long sleeved cotton or fire retardant shirt, long fire retardant  pants, closed-toe shoes and a hardhat with attached Hazard Risk Category 2 Arc Flash Faceshield rated at 15cal/cm

  - In addition, use whatever PPE that is prescribed by RadCon, if they require it.

- Identify danger zones

  - Within the Electrical Shock Hazard Limited Approach Boundary and the Arc Flash Hazard Flash Protection Boundary which are both delineated by the power supply platform yellow handrails and the personnel access gate at the stairs.

- Number of people needed

  - Two qualified electrical workers are required to Lock, Tag and Try the power supply.  After it is locked out:  1 electrical/electronic or mechanical tech and qualified electrical worker, with the following minimal training:  Rad Worker I; Jlab Lock, Tag and Try;  Hall A Safety Walkthrough

- List of materials

  - None

- Procedure

  - Observe the power supply control panel.  If the “Main Power” lamp is green, observe the display panel – “SET” should be all zeros.  If it is not zeros, go to the Controls Interface Terminal next to the green steel block wall and select the Q1 power supply gui from the “Hall A General Tools” gui.  Type in zeros into the “Setpoint” box, and press enter.  Go back to the power supply control panel display.  The “SET” and “ADC” (which reads in per cent – with .999999999 being the maximum) should read zeros, but a small amount of offset is normal in the “ADC” reading.

  - Once the “ADC” reading is zeros, push the “local/remote” button to extinguish the remote control lamp.  The “Main Power” lamp should extinguish; if it does not, push the “Main Power Off” button.

  - Turn off and Lock, Tag and Try the input power from the disconnect switch marked “PQ17(1 or 2) in accordance with all current Jlab Lock, Tag and Try regulations, and in accordance with the procedure detailed in the SOP which is attached to the Control Panel door.  After the disconnect switch is locked out, attempt to turn on the power supply from the Control Panel.  The Control Panel should be completely “dead”.

  - Open the door next to the Control Panel door.  Locate the ZFCT electronics box about chest-height.  It is labeled with the words “Danfysik” and “Ultrastab System 861R”.

  - Reach behind the ZFCT box and unplug all of the cords and connectors.  Alternatively,  you may find it easier to reach the plugs from the opposite door.

  - Remove the rack mount screws from the front panel of the ZFCT box.  Slide it out of its mount, and put it on a work surface.

  - Remove the lid screws, and remove the lid.  Observe if there is any visible dust accumulation on the internal fans and or heat sinks.  Stop work if any dust is found, and call Radcon for assistance.  A Radcon technician will take a swipe of the dust and determine if they must become involved in the cleaning operation.  Follow the instructions of the Radcon technician.

  - If the Radcon tech clears the cleaning operation, use a vacuum cleaner or other means to remove the dust.  The goal here is to restore the functionality of the heat sink and fans, which cannot work if they are clogged with dust.

  - Reassemble the lid onto the ZFCT box.

  - Reinstall the ZFCT box into the power supply, and reconnect the cables.

  - Close and lock all power supply doors.

  - Unlock. And restore electrical power to the power supply.

  - Test the power supply for normal operation.

- Post job briefing and cleanup

5. Provide feedback and continuous improvement. (Document any mistakes, corrections, changes and pictures and implement changes.)