Operational Safety Procedure (OSP)

Expiration Date: ________________

Division serial number _______________

(Assigned by division EH&S officer when complete)

| Issue Date: |  |
| --- | --- |
| Expiration Date: No more than three years from Issue Date |  |
| Title: Maintenance, testing and diagnosis of the Q 2/3 power supplies |  |
| Location: Hall A |  |
| Risk classification (See EH&S Manual Chapter 3210 Hazard Identification and Characterization.) | Without mitigation measures :3 |
|  | With specified measures implemented : 0 |
| Author(s): Ed Folts, Jack Segal | Date: 3/3/09 |

Supplemental technical validations:

| Hazard reviewed: | Reviewer signature: | Date: |
| --- | --- | --- |
| William Vulcan |  |  |

Signatures:									Date:

| Division EH&S Officer, recommendation: | Charles Hightower |  |
| --- | --- | --- |
| Department manager approval: | Dennis Skopik |  |
| Department or group approval: | Kees deJager |  |
| Other approval(s): |  |  |

Document History:

| Revision: | Reason for revision: | Serial number of superseded OSP |
| --- | --- | --- |

Distribution:

Copies to: affected area, authors, division EH&S officer, EH&S Reporting Manager

(After expiration, forward original to the EH&S Reporting Manager for archiving.)

1. Define the scope of work

- Job Summery

Maintenance, testing and diagnosis of the Hall A Q 2/3 power supplies

- Affected systems

Q 2/3 power supply, its controls and interlocks

Access to the power supply balcony

2. Analyze Hazard

Task Hazard Analysis Worksheet

A-08-098-T									Date 5/2/08

| Complete all information. Use as many sheets as necessary. |  |
| --- | --- |
| Task location: Hall A, Q 2/3 power supplies | Task title: General work in Q 2/3 magnet power supplies |
| Division Physics | Prepared by: Folts |
| Department Hall A | Reviewed by |
| Supervisor de Jager | Approved by Folts |
| Standard Requirements: (PPE, TOSPs, SOPs, etc.) |  |

| Task | Potential Hazards | Risk Code before mitigation | Safe Procedures/Practices/Controls | Risk Code after mitigation |
| --- | --- | --- | --- | --- |
| General work in Q2/Q3 magnet power supplies after locked and tagged Work in low voltage (controls) section of the Q2/3 magnet power supplies Diagnostics in the Q2/3 magnet power supplies while energized | Electrical flash, shock hazard Electrical shock from capacitors Shock from energy stored in magnet Radioactive contamination hazard | 4 3 3 3 | Lock, Tag and Try the source of electrical energy in accordance with JLAB Lock, Tag and Try regulations and by following this OSP Proper PPE In accordance with this procedure In accordance with the standing Radiation Work Permit, Radcon personnel will survey the dust present for radioactive contamination and if required write a Radiation Work Permit for the job. | 0 0 |

3. Develop and implement Hazard controls

- List of PPE

List of PPE for working in controls with guards in place:		None

List of PPE for working in controls with guards removed:

Safety glasses

Flame resistant long pants and long sleeve shirt

List of PPE for safeing power supplies and performing diagnostics on energized power supply is:								Safety glasses

Flame resistant long pants and long sleeve shirt

Meters rated to at least CAT IV for 480V

- Identify danger zones

When the power supplies are being worked on the gate at the top of the access stairs will be closed and the area will be restricted to trained and necessary personnel.

- Training required

Access to the power supplies and the power supply balcony will be restricted to personnel that have the required training including electrical worker training, Rad II, and equipment specific training.

4. Perform work within controls

- Number of people needed

While doing diagnostics or safeing the power supply 2 people are needed.

- Verify  that needed training is completed and current

Qualified electrical worker

- List of materials

As required for the task

- Procedures

Depowering and safeing the power supply

Perform pre-job briefing and ensure training of personnel.

Ramp the magnet power to 0 and turn off power supply.

Lower the contactor arm on the front of the power supply.

Using the VVU on the wall mounted disconnect switch insure that there is power to the power supply.

While wearing long sleeves, long pants and safety glasses turn off the circuit breakers on the front of the power supply.

While wearing long sleeves, long pants and safety glasses turn power off at the wall mounted disconnect switch and lock out the switch using lock and tag procedures.

Use the VVU to insure that the power has been shut down.

Verify that the power is disconnected by turning on the circuit breakers and attempting to restart the supply. Turn off the circuit breakers.

Close gate at the access point to the power supply balcony.

While wearing long sleeves, long pants and safety glasses open the door to the power supply and use the shorting probe to ground the magnet power cables and the capacitor banks at the capacitor grounding panel.

Engage grounding bar at the capacitor grounding panel.

Notify Radcon that the power supply is open and have it cleared by them prior to beginning work.

Restarting the power supply

Ensure that all components are reinstalled and secure. If the work was extensive, this should be done by a second person.

Remove and secure the grounding bar.

Close all doors.

While wearing safety glasses, long pants and long sleeves remove locks and turn on power at the wall mounted disconnect switch.

While wearing safety glasses, long pants and long sleeves turn on the circuit breakers and raise the contactor arm on the front of the power supply.

Clear the final interlock and turn the power supply on.

Open gate.

Ramp the power supply to desired current.

Working on controls (low voltage)

Perform pre-job briefing and ensure training of personnel

Do not remove finger guards while this power supply is energized

Performing diagnostics

Perform pre-job briefing and ensure training of personnel.

Proper PPE for energized diagnostics includes; safety glasses, flame resist long pants and long sleeve shirt, meters rated to at least CAT IV for 480V testing.

Diagnostics includes measurements only. NO manipulation of components is allowed during a diagnosis.

- Post-job briefing and cleanup

5. Provide feedback and continuous improvement.

Document any mistakes, corrections, changes and pictures and implement changes. Turn in feedback to Hall work coordinator

List of qualified personnel

Name					Signature				Date

Segal

Spiegel

Fansler

Dezern

Ewing

Folts

Gomez

Vulcan											
Merz

Wood