Hall A Planned Maintenance Task:  .;

1. Define the scope of work
	Replace socketed chips on Q1 Danfysik power supply control panel

2.  Analyze Hazard

| Task | Potential Hazards | Risk Code before mitigation | Safe Procedures/Practices/Controls | Risk Code after mitigation |
| --- | --- | --- | --- | --- |
| Replace all socketed chips on control panel board. | Low voltage electrical shock | 0 | Turn off power before changing chips | 0 |

3. Develop and implement Hazard controls

Turn off power before changing chips

4. Perform work within controls (follow procedure)

- Summary of job

  - Replace socketed chips on Q1 power supply control panel.;

- List of PPE

  - None required

- Identify danger zones

  - An area extending 36 inches out from the Q1 Danfysik power supply control closet door,  when power is applied to the power supply.

- Number of people needed

  - 1 electrical/electronic or mechanical tech and qualified electrical worker, with the following minimal training:  Rad Worker I; Jlab Lock, Tag and Try;  Hall A Safety Walkthrough

- List of materials

  - The following chips or components:  H11L1, qty. 2;  UA9638, qty. 1;  UA9637, qty. 1;  HY6264, qty. 1;   Z86E2112PSC, qty. 1;  also Siemens light reflecting switches, SFH900-2, qty. 2 IC 20 and 21, (soldered).

- Procedure

  - Observe the power supply control panel.  If the “Main Power” lamp is green, observe the display panel – “SET” should be all zeros.  If it is not zeros, go to the Controls Interface Terminal next to the green steel block wall and select the Q1 power supply gui from the “Hall A General Tools” gui.  Type in zeros into the “Setpoint” box, and press enter.  Go back to the power supply control panel display.  The “SET” and “ADC” (which reads in per cent – with .999999999 being the maximum) should read zeros, but a small amount of offset is normal in the “ADC” reading.

  - Once the “ADC” reading is zeros, push the “local/remote” button to extinguish the remote control lamp.  The “Main Power” lamp should extinguish; if it does not, push the “Main Power Off” button.

  - Turn off power at the safety disconnect switch marked PQ17(1 or 2).

  - Open the control panel door.

  - Locate the Control Panel, part no. P-82038.  Disconnect the dsub connector from the back of the Control Panel.  Remove the Control Panel and take it to a solder station.

  - Replace the following socketed chips:  H11L1, qty. 2;  UA9638, qty. 1;  UA9637, qty. 1;  HY6264, qty. 1;   Z86E2112PSC, qty. 1.  Unsolder and replace the two Siemens optical switches, SFH900-2, qty. 2.

  - Reinstall the Control Panel into the power supply.

  - Close and lock the control panel door.

  - Restore power to the power supply.

  - Test power supply for normal operation.

- Post job briefing and cleanup

5. Provide feedback and continuous improvement. (Document any mistakes, corrections, changes and pictures and implement changes.)