The right Q1 liquid level displayed “inf” on the tools GUI, but was

correct on the cryo page. We rebooted the right IOC, no joy. We

cycled power on the magnet, no joy. I went in on friday to look at

one of the channels in the HP1313.  HacR_HPE1313A:0_Ch18

which is supposed to be the helium level readout for Right Q1.

By the time I was done I was seeing about 8 volts at the terminal

block.  From there it goes to the VME crate.  Also,

HacR_HPE1313A:0_Ch19 has 3.17 volts on its input.  Channels HacR_HPE1313A:0_Ch12 through HacR_HPE1313A:0_Ch20 do

not seem to be active.  Only Ch18 and Ch19 have anything connected

to their inputs, the rest should have the varying noise we get on a

floating input. All those channels seem to not be updating. 
Heidi had noticed this before, I was trying to verify what 
she saw.    The only other thought would be that the voltage is

not appearing at the VME crate, which I did not have time to check.

But, it really looks like things might just not be scanning the 
channels.